## READ ME (hidden)
GENERAL INSTRUCTIONS
● | The technology factsheet contains information about one specific option (e.g. capacity, potential, costs, energy and emission effects and supporting descriptions).
● | The factsheet should be filled-in by technical experts in the technology field and used as a reference internally (e.g. input for OPERA model) and externally.
● | The data in the technology factsheet is for technology options in the Netherlands and could be used for EU countries.
● | A regular update of technology factsheet is required every 3-5 years.
● | Read carefully the definitions and instructions for each parameter below and fill-in all data in the 'Data input' tab. The data will be automatically allocated in the factsheet (see 'Factsheet' tab).
● | The 'Factsheet' tab is locked. If a change is necessary, please send a request to Silvana Gamboa or Koen Smekens.
→ | READ ME: Definitions of parameters and instructions. Units and conversions factors (incl. monetary conversions) are also found below.
→ | Data input: Technology factsheet data to be filled-in by the expert.
→ | Technology Factsheet: Factsheet filled-in automatically from the data in the 'Data input' tab. This tab is protected.
→ | List: Lists of sectors, units, energy carriers, etc. that are used in the 'Data input' tab (drop-down menu's)
→ | Calculations: Here, calcuations, screen-shots and other references can be placed to back-up the data of the factsheet. Please note that the information placed here will not be included in the Technology Factsheet for disclosure.
→ | Visual representation: A relevant visual representation of the technology can be placed here. The image will be placed in the final technology factsheet to be disclosed.
| PARAMETER | DEFINITION |  | HOW TO FILL-IN THE FACTSHEET?
| Sector | ● | To which sector the technology belongs to (according to OPERA classification). | ● | Select the sector from the drop-down menu. If the sector is not available in the menu, please specify in the field 'Other'.
|  |  |  | ● | New sectors can be added to the drop-down menu within the tab 'List' upon request.
| ETS / Non-ETS | ● | Indicate if the technology falls within the Emissions Trading Scheme (ETS).
| Type of Technology | ● | Examples: renewable, saving, CCS, biomass, emission reduction, network (e.g. transformer), etc. | ● | Select the type of technology from the drop-down menu. New types of technologies can be added within the tab 'List' upon request.
| Description | ● | Description of the technology, including technology boundaries, components, applications, etc. | ● | The description is limited up to 700 characters.
| TRL | ● | Select the Technology Readiness Level (TRL) for 2020 based on the assessment below: | ● | Please specify data sources in the explanation box.
NASA/DOD Technology Readiness Level
|  | TRL 9 | Actual system 'flight proven' through succesful mission operations
|  | TRL 8 | Actual system completed and 'flight qualified' through test and demonstration
|  | TRL 7 | System prototype demonstration in space environment
|  | TRL 6 | System/subsystem model or prototype demonstration in a relevant environment (ground or space)
|  | TRL 5 | Component and/or breadboard validation in relevant environment
|  | TRL 4 | Component and/or breadboard validation in laboratory environment
|  | TRL 3 | Analytical and experimental critical function and/or characteristic proof-of-concept
|  | TRL 2 | Technology concept and/or application formulated
|  | TRL 1 | Basic principles observed and reported
TECHNICAL DIMENSIONS
| Factsheet Functional Unit | ● | Unit in which the capacity for production of the main output is expressed e.g. Mton or PJ | ● | The Factsheet Functional Unit chosen provides a reference for the other parameters (i.e. capacity) in order to keep consistency through the factsheet.
|  |  |  | ● | Select the functional unit from the drop-down menu. Conversion factors are found at the bottom of this tab (please specify in the explanation box if other conversion factors are used).
| Capacity | ● | The typical technology capacity size or sizes if there is clear size dependent data. | ● | Technologies that differ largely in size (e.g. large and small scale) must be placed in different factsheets.
|  |  |  | ● | Specify the Capacity value and its respective reference from up to 5 different data sources. Please aggregate all sources in the references and sources box at the bottom of 'Data input' tab.
|  |  |  | ● | Data ranges (min,max) will be automatically allocated in the factsheet.
| Potential | ● | How much of the technology option can be installed in The Netherlands or EU? | ● | Specify the Potential value and its respective reference from up to 5 different data sources. Please aggregate all sources in the references and sources box at the bottom of 'Data input' tab.
|  |  |  | ● | Select which region is covered for the potential from the drop-down menu.
| Market share (Deployment share) | ● | Current market share and maximum expected market share in the future (2030 and 2050). | ● | Market share can be optional for some technologies, in that case, please specify the Potential instead or vice-versa.
|  | ● | Only for competing technologies e.g. heat supply appliances for households such as heat pumps with a market share of 80% of the households. | ● | Specify the Market share and its respective reference from up to 5 different data sources. Please aggregate all sources in the references and sources box at the bottom of 'Data input' tab.
| Capacity utilization factor | ● | The capacity utilization factor is the percentage of the total capacity that is actually being utilized e.g. capacity expansion to absorb additional renewable electricity or over-dimensioning. | ● | If the capacity utlization factor is not filled-in, the value will be automatically assigned as one.
| Full-load running hours per year | ● | The typical number of hours that the technology in question operates per year.
| Unit of Activity | ● | Unit of annual production (output) per year | ● | Select the activity unit from the drop-down menu.
| Activity (Cap2Act) (Optional) | ● | Actual annual production (output) per year | ● | Specify the value for Activity.
|  | ● | Activity = Capacity*Load Factor | ● | Only relevant for infrastructure technologies (e.g. the amount of energy per hour that can be delivered)
| Technical lifetime (years) | ● | The total amount of years during which the technology can technically perform/function before it must be replaced.
| Progress ratio | ● | Progress ratio (PR) is the cost reduction factor achieved by a doubling of the cumulative installed capacity of a technology. Learning rate (LR) = 1 – PR The underlying formula is : Ci= α*Ccumi^b Ci = cost of unit i α = constant (cost unit 1) Ccumi = Cumulative capacity at time of unit i b = learning elasticity A doubling of total cumulative capacity reduces specific costs by a factor of 2b. In the usual case where b is negative, 2b (labelled the progress ratio, PR) is between zero and one. The complement of the progress ratio (1-PR) is called the learning rate (LR). A learning elasticity (b) of -0.32, for example, yields a progress ratio of 0.80 and a learning rate of 20%. This means that the specific capital cost of newly installed capacity decreases by 20% for each doubling of total installed capacity. On a double-logarithmic scale, the decrease in costs appears as a straight line.
| Hourly profile | ● | Is there an hourly profile for the technology? | ● | Select YES/NO
COSTS
| Year of Euro | ● | All costs data must be specified as €2015 | ● | If amounts are expresed in other currencies or in euros of another year (e.g. €2016), the amount has to be converted. See Monetary conversions at the bottom of the tab.
| Investment costs | ● | Total investment costs (CAPEX) in (million) euro in 2020, 2030 and 2050 per functional unit (e.g. per MW, per PJ). | ● | Specify the Costs and their respective reference for 2020(current), 2030 and 2050 from up to 5 different data sources. Please aggregate all sources in the references and sources box at the bottom of 'Data input' tab.
|  | ● | The investments costs are in the case of a new application of the technology. This includes purchase costs, construction costs, net equipment costs and installation costs. Excludes indirect costs, design and site-specific costs. | ● | Specify in the costs explanation box what specifically is included in the investment costs.
|  |  |  | ● | The costs should not be annualized. Site-specific costs (greenfield/brownfield), pre-design costs, pre-construction costs, financing costs should be extracted from the total value.
| Other costs | ● | E.g. electricity connection costs, demolition and removal costs of decommissioned installations. | ● | Please specify Other costs within the Costs explanation box.
|  |  |  | ● | Data input same as above.
| Fixed operational costs (excluding fuel costs) | ● | Fixed operational costs are per year. | ● | Data input same as above.
| Variable costs (excluding fuel costs) | ● | Variable costs are per year. | ● | Data input same as above.
ENERGY IN- AND OUTPUTS
| Energy carriers | ● | Input/output of energy carriers per unit of the main output. The technology may consume/produce more than one input/output. | ● | Select the energy carrier from the drop-down menu (please specify the main output first). Other energy carriers can be added within the tab 'List' upon request.
|  | ● | For each technology, the amount of energy input/output to the process have to be filled in. The process may require more than one input e.g. available waste heat streams can be described as energy outputs or captured CO2 can also be seen as an output). | ● | Specify the values in PJ for 2020, 2030 and 2050 with their respective references from up to 5 different data sources. Please aggregate all sources in the references and sources box at the bottom of 'Data input' tab. Values should be expressed as a ratio per unit of main output whereas inputs should be expressed as positive and values for outputs as negative.
|  |  |  | ● | The value should correspond 'per unit of output' (e.g. output of natural gas with 60% efficiency). Explain the details (i.e. efficiency) in the explanation box.
MATERIAL FLOWS (Optional)
| Material flows | ● | Optional except for technologies with activity level associated e.g. iron, steel, ammonia production, ethylene, ethene. | ● | Specify the material flows and units and add the values for 2020, 2030 and 2050 withtheir respective references from up to 5 difference data sources. Please aggregate all sources in the references and sources box at the bottom of 'Data input' tab.
EMISSIONS
| Emissions | ● | Non-fuel/energy-related emissions or emissions reductions (e.g. CCS) | ● | Select the substance and unit from the drop-down menu. Other emissions can be added within the tab 'List' upon request.
|  |  |  | ● | Specify the Emissions for 2020, 2030 and 2050 with their respective references from up to 5 difference data sources. Please aggregate all sources in the references and sources box at the bottom of 'Data input' tab.
OTHER (Optional)
| Other | ● | Extra relevant parameters for specific technologies e.g. charge/discharge time for batteries, efficiency, etc. | ● | Specify the parameter and unit adding more details in the explanations box below the sub- section. Here, you can specify the relevance of this parameter for the specific technology and references.
|  |  |  | ● | You may add one single value in the main reference for 2020 (current) or add values for 2020, 2030 and 2050 with their respective references from up to 5 difference data sources. Please aggregate all sources in the references and sources box at the bottom of 'Data input' tab.
REFERENCES AND SOURCES
| ● | For data values: Add references for each value in their 'Reference' cell (i.e. author and year) and aggregate all references with complete description at the bottom of the 'Data input' tab (in order of importance). If more than 10 references, add other sources under 'Others' box.
| ● | For complementary data and text: Add all data sources with complete description at the bottom of the 'Data input' tab (in order of importance or mostly used). You may link these references with text in the explanatory boxes. If more than 10 references, add other sources under 'Others' box.
UNITS
| Bln vehicle - km |  | Use this unit to represent transport technologies
| GWe |  | Gigawatt electrical
| kton |  | Kiloton
| Mton |  | Megaton
| Mton ethene |  | Megaton ethene
| Mton NH3 |  | Megaton Ammonia
| Mton steel |  | Megaton steel
| Mvtg |  | Million vehicles
| PJ |  | PetaJoule
CONVERSION FACTORS
| COMMON CONVERSIONS |  | 1 MJ = 106 Joule
1 GJ = 109 Joule
1 TJ = 1012 Joule
1 PJ = 1015 Joule
1 MWh = 3,6 GJ
1 GWh = 3,6 TJ
1 TWh = 3,6 PJ
| OTHER CONVERSIONS |  | The International Energy Agency offers a converter for energy units, you can find the converter in the link below:
https://www.iea.org/statistics/resources/unitconverter/
| MONETARY CONVERSIONS | ● | If amounts are expresed in other currencies or in euros of another year (e.g. €2016), the amount has to be converted.
|  | ● | A standard method to correct for inflation is to use the Harmonised Index of Consumer Prices (HICP) (see below). To convert an amount expressed in €2014 to €2017, it has to be multiplied by a factor (HICP 2017/ HICP 2014) = (101,40/99,79) = 1,016.
Harmonised Index of Consumer Prices (HICP) for the Netherlands:
HICP (2015 =100)
|  | 2010 | 92.05
|  | 2011 | 94.32
|  | 2012 | 96.99
|  | 2013 | 99.47
|  | 2014 | 99.79
|  | 2015 | 100
|  | 2016 | 100.11
|  | 2017 | 101.4
|  | 2018* | 104.37
*As of August, 2018 - Follow update here: https://goo.gl/rvWufC
Statistics Netherlands (CBS), “Consumentenprijzen; Europees geharmoniseerde prijsindex 2015=100”

## Data input (old) (hidden)
FACTSHEET DATA INPUT
Please fill-in here all technology option data including detailed references and sources at the bottom.
TECHNOLOGY DESCRIPTION
| Name of technology option |  | Diabatic compressed air energy storage (CAES) for large-scale temporal electricity storage
| Date of factsheet |  | 2020-02-20
| Sector |  | Electricity generation
Other (specify here)
| ETS / Non-ETS |  | Non-ETS
| Type of Technology |  | Storage
| Description |  | Compressed air energy storage (CAES) is based on storing electricity as compressed air. Compressed air is typically stored underground in suitable geological formations (salt, hard rock and porous rock or aquifer). Aboveground CAES is also a possibility, however investment costs in this case are higher. This factsheet only considers underground CAES whereas air is expanded through a turbine to produce electricity. Diabatic CAES uses fuel (typically natural gas) to heat the expanding air (JRC ETRI, 2014). CAES is typically a large-scale, long-term storage option, and it is applied on the centralised grid. As of 2017, there are two large diabatic CAES projects installed globally, the first one is a 290 MW plant in Germany, and the second one is a 110 MW plant in Alabama, the US (DNV KEMA, 2013; IRENA, 2017). | [17 empty] | Compressed air energy storage (CAES) is based on storing electricity as compressed air. Compressed air is typically stored underground in suitable geological formations (salt, hard rock and porous rock or aquifer). Aboveground CAES is also a possibility, however investment costs in this case are higher. This factsheet only considers underground CAES whereas air is expanded through a turbine to produce electricity. Diabatic CAES uses fuel (typically natural gas) to heat the expanding air (JRC ETRI, 2014). CAES is typically a large-scale, long-term storage option, and it is applied on the centralised grid. As of 2017, there are two large diabatic CAES projects installed globally, the first one is a 290 MW plant in Germany, and the second one is a 110 MW plant in Alabama, the US (DNV KEMA, 2013; IRENA, 2017).
| TRL level 2020 |  | TRL 9
|  |  | The two large existing projects were already installed in 1978 (Germany) and in 1991 (Alabama) (DNV KEMA, 2013). More plants are being prepared, such as a plant in Larne, Ireland (TNO, 2018). | [17 empty] | The two large existing projects were already installed in 1978 (Germany) and in 1991 (Alabama) (DNV KEMA, 2013). More plants are being prepared, such as a plant in Larne, Ireland (TNO, 2018).
TECHNICAL DIMENSIONS
| Factsheet Functional Unit |  | kWh
|  |  | Functional Unit |  |  | Main Source | Source 2 | Source 3 | Source 4 | Source 5
| Capacity |  | kWh |  |  | 3000000 | 580000 | 2860000
[6 empty] | JRC ETRI 2014 | Luo et al. 2015 | Luo et al. 2015 | Reference | Reference
|  |  | Context |  | Unit | 2020 (Current) |  |  |  |  | 2030 |  |  |  |  | 2050
| Potential |  | NL |  | GWh | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5
550
[6 empty] | TNO 2018 | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
| Market share |  | Global utility scale electricity storage |  | % | 0.3%
[6 empty] | IRENA 2015 | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
| Capacity utilization factor |  | Specify here (if not specified, value will be 1)
| Full-load running hours per year |  | Specify here
| Unit of Activity |  | PJ/year
| Activity (Cap2Act) (Optional) |  | Specify here
| Technical lifetime (years) |  | 30 years (IEA ETSAP & IRENA, 2012), 40-55 years (JRC ETRI, 2014). Up to 200,000 cycles (DNV KEMA, 2013)
| Progress ratio |  | N/A (JRC ETRI, 2014)
| Hourly profile |  | No
| Explanation |  | Project specifications determine capacity and detailed project design. An example from TNO (2018): 100 MW/2,860 MWh (26h discharge time) with a cavern of 538.000 m3. Assuming charge time is similar to discharge time (26h), then the compressor capacity required will be 350 m3/s. If faster charge times are desired, a larger compressor is required. The potential estimated by TNO is 50% of the theoretical storage potential in onshore salt caverns in the Netherlands. These salt caverns can also be used for natural gas or hydrogen storage and may therefore not be completely available for CAES (TNO, 2018). As of 2015, the global grid-connected CAES capacity is 440 MW (0.3%) and it is the largest installed utility scale storage after pumped hydro. Pumped hydro dominates the large-scale electricity storage market with over 140 GW installed capacity (99.1% of installed capacity) (IRENA, 2015). More projects are under development (TNO, 2018). Reports on lifetime vary from 30 years (IEA-ETSAP & IRENA, 2012), to 40-55 years (JRC ETRI, 2014), and to 20-100 years (IRENA, 2017). | [17 empty] | Project specifications determine capacity and detailed project design. An example from TNO (2018): 100 MW/2,860 MWh (26h discharge time) with a cavern of 538.000 m3. Assuming charge time is similar to discharge time (26h), then the compressor capacity required will be 350 m3/s. If faster charge times are desired, a larger compressor is required. The potential estimated by TNO is 50% of the theoretical storage potential in onshore salt caverns in the Netherlands. These salt caverns can also be used for natural gas or hydrogen storage and may therefore not be completely available for CAES (TNO, 2018). As of 2015, the global grid-connected CAES capacity is 440 MW (0.3%) and it is the largest installed utility scale storage after pumped hydro. Pumped hydro dominates the large-scale electricity storage market with over 140 GW installed capacity (99.1% of installed capacity) (IRENA, 2015). More projects are under development (TNO, 2018). Reports on lifetime vary from 30 years (IEA-ETSAP & IRENA, 2012), to 40-55 years (JRC ETRI, 2014), and to 20-100 years (IRENA, 2017).
COSTS
| Reference year: €2015 - If amounts are expresed in other currencies or in euros of another year (e.g. €2014), the amount has to be converted. See conversion method in 'READ ME' tab. Costs are per unit of output. |  |  |  |  | 2020 (Current) |  |  |  |  | 2030 |  |  |  |  | 2050
[6 empty] | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5
| Investment costs |  | € / | kWh |  | 35 | 46 | 50 | 2 | 40 | 31 | 38 | 40 |  |  | 26
[6 empty] | JRC ETRI 2014 | IRENA 2017 | FCH JU McKinsey 2015 | Chen et al. 2009 | Chen et al. 2009 | JRC ETRI 2014 | IRENA 2017 | FCH JU McKinsey 2015 | Reference | Reference | JRC ETRI 2014 | Reference | Reference | Reference | Reference
| Other costs per year |  | € / | kWh
[6 empty] | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
| Fixed operational costs per year (excl. fuel costs) |  | € / | kWh |  | 0.455 | N/A | 1.01 | N/A | N/A | 0.403 | N/A | 0.8 |  |  | 0.338
[6 empty] | JRC ETRI 2014 | IRENA 2017 | Own calculation based on FCH JU McKinsey 2015 | Chen et al. 2009 | Chen et al. 2009 | JRC ETRI 2014 | IRENA 2017 | FCH JU McKinsey 2015 | Reference | Reference | JRC ETRI 2014 | Reference | Reference | Reference | Reference
| Variable costs per year (exc. Fuel costs) |  | € / | MWh |  | 1.21 | N/A | 30 | N/A | N/A | 1.21 | N/A | 30 |  |  | 1.21
[6 empty] | JRC ETRI 2014 | IRENA 2017 | FCH JU McKinsey 2015 | Chen et al. 2009 | Chen et al. 2009 | JRC ETRI 2014 | IRENA 2017 | FCH JU McKinsey 2015 | Reference | Reference | JRC ETRI 2014 | Reference | Reference | Reference | Reference
| Costs explanation |  | There are significant degrees of freedom in designing (diabetic) CAES system, such as pump size and turbine size which determine in combination with the reservoir size the charge and discharge times and the energy/power ratio. Design choices such as these influence system costs, which means there are relatively large ranges in costs possible. The sources used have been chosen because they are recent publications and include projections up to (at least) 2030. JRC ETRI (2014) is used as primary source because it has the most complete set of data, including CAPEX and FOM/VOM estimates up to 2050. Details of the cost estimates are not, or only shortly, elaborated in these reports, and estimations of investment costs from other sources vary from 2 €/kWh to 500 €/kWh. Data points for the current year (2020) differ per source: 2020 for JRC ETRI (2014), 2016 for IRENA (2017), 2013 for JCH JU McKinsey (2015), and 2009 for Chen et al. (2009). The main FOM costs calculated using the JRC ETRI (2014) assumption that they represent 1.3% of investment costs. It is assumed that FOM costs remain 1.3% of investment costs in 2020, 2030 and 2050. Other FOM costs are from FCH JU Mckinsey (2015) that states FOM costs as 15 €/kW/year in 2013 and 12 €/kW/year in 2030. These have been calculated to M€/GWh/year assuming a standard storage capacity of 15 hours (200MW/3000MWh system - JRC ETRI, 2014). VOM costs are only provided for 2013 by JRC ETRI (2014) and it is assumed the they remain the same in 2020, 2030 and 2050. VOM costs are defined by JRC ETRI (2014) as production-related O&M costs that vary with electrical generation. They exclude personnel, fuel, and CO2 costs. | [18 empty] | There are significant degrees of freedom in designing (diabetic) CAES system, such as pump size and turbine size which determine in combination with the reservoir size the charge and discharge times and the energy/power ratio. Design choices such as these influence system costs, which means there are relatively large ranges in costs possible. The sources used have been chosen because they are recent publications and include projections up to (at least) 2030. JRC ETRI (2014) is used as primary source because it has the most complete set of data, including CAPEX and FOM/VOM estimates up to 2050. Details of the cost estimates are not, or only shortly, elaborated in these reports, and estimations of investment costs from other sources vary from 2 €/kWh to 500 €/kWh. Data points for the current year (2020) differ per source: 2020 for JRC ETRI (2014), 2016 for IRENA (2017), 2013 for JCH JU McKinsey (2015), and 2009 for Chen et al. (2009). The main FOM costs calculated using the JRC ETRI (2014) assumption that they represent 1.3% of investment costs. It is assumed that FOM costs remain 1.3% of investment costs in 2020, 2030 and 2050. Other FOM costs are from FCH JU Mckinsey (2015) that states FOM costs as 15 €/kW/year in 2013 and 12 €/kW/year in 2030. These have been calculated to M€/GWh/year assuming a standard storage capacity of 15 hours (200MW/3000MWh system - JRC ETRI, 2014). VOM costs are only provided for 2013 by JRC ETRI (2014) and it is assumed the they remain the same in 2020, 2030 and 2050. VOM costs are defined by JRC ETRI (2014) as production-related O&M costs that vary with electrical generation. They exclude personnel, fuel, and CO2 costs.
ENERGY IN- AND OUTPUTS
| Values expressed as a ratio per unit of main output. Inputs as positive and outputs as negative. |  | Energy carrier |  | Unit | 2020 (Current) |  |  |  |  | 2030 |  |  |  |  | 2050
[6 empty] | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5
| Energy carriers (per unit of main output) |  | Electricity |  | PJ | -1
[6 empty] | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
|  |  | Electricity |  | PJ | 0.77
[6 empty] | Calculated based on Huang et al 2017 | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
|  |  | Natural gas |  | PJ | 1.13
[6 empty] | Calculated based on Huang et al 2017 | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
|  |  | Please select |  | PJ
[6 empty] | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
| Energy in- and Outputs explanation |  | The required amounts of electricity and natural gas are stated to obtain 1 PJ of electrical output - based on Huang et al (2017). Note that the output of electricity is higher than the input due to the addition of heat from the combustion of natural gas. Total efficiency is 53% in this configuration, which is at the high end of the 42-54% range reported by DNV KEMA (2013). | [18 empty] | The required amounts of electricity and natural gas are stated to obtain 1 PJ of electrical output - based on Huang et al (2017). Note that the output of electricity is higher than the input due to the addition of heat from the combustion of natural gas. Total efficiency is 53% in this configuration, which is at the high end of the 42-54% range reported by DNV KEMA (2013).
MATERIAL FLOWS (OPTIONAL)
| Material flows |  | Material |  | Unit | 2020 (Current) |  |  |  |  | 2030 |  |  |  |  | 2050
[6 empty] | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5
|  |  | Specify here |  | Specify here
[6 empty] | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
|  |  | Specify here |  | Specify here
[6 empty] | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
| Material flows explanation |  | Explain here | [18 empty] | Explain here
EMISSIONS (Non-fuel/energy-related emissions or emissions reductions (e.g. CCS)
| Emissions |  | Substance |  | Unit | 2020 (Current) |  |  |  |  | 2030 |  |  |  |  | 2050
[6 empty] | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5
|  |  | Please select |  | Please select
[6 empty] | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
|  |  | Please select |  | Please select
[6 empty] | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
|  |  | Please select |  | Please select
[6 empty] | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
|  |  | Please select |  | Please select
[6 empty] | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
| Emissions explanation |  | Explain here (e.g. emission factors if calculated) | [18 empty] | Explain here (e.g. emission factors if calculated)
OTHER
| Specify below the other relevant parameters for the specific technology |  | Unit |  |  | 2020 (Current) |  |  |  |  | 2030 |  |  |  |  | 2050
[6 empty] | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5
| Depth of discharge |  | % |  |  | N/A
[6 empty] | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
| Charge time |  | Hours |  |  | 26
[6 empty] | TNO 2018 | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
| Discharge time |  | Hours |  |  | 15 | 2 | 6 | 26
[6 empty] | Based on JRC ETRI 2014 | TNO 2018 | TNO 2018 | TNO 2018 | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
| Self discharge |  | % / month |  |  | 0
[6 empty] | DNV-KEMA 2013 | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
| Explanation |  | Charge and discharge times are project dependent (see explanation in technical dimensions section). JRC ETRI (2014) states that the minimum time necessary to charge a unit is approximately 8 minutes. TNO (2018) gives the example of 26 hours charge time as stated above. The main discharge time is based on the size of typical system as reported by JRC ETRI (2014) - 200MW/3,000MWh. TNO (2018) compares three plants (Huntdorf (DE), McIntosh (US), and Larne (IE)) with varying specifications (Huntdorf capacity is ca. 300 MW and 600 MWh and McIntosh capacity is ca. 110 MW and 2,860 MWh). Capacity, charge time, and discharge time depend, amongst other things, on cavern size and the specifications of the turbine and compressor used for the project.
REFERENCES AND SOURCES
| 1 | JRC 2014. Energy Technology Reference Indicators (ETRI) projections for 2010-2050 | [19 empty] | JRC 2014. Energy Technology Reference Indicators (ETRI) projections for 2010-2050
| 2 | DNV-KEMA 2013. Systems Analysis Power to Gas (deliverable 1: Technology review) | [19 empty] | DNV-KEMA 2013. Systems Analysis Power to Gas (deliverable 1: Technology review)
| 3 | IRENA 2017. Electricity Storage Costs | [19 empty] | IRENA 2017. Electricity Storage Costs
| 4 | Luo et al. (2015). Overview of current development in electrical energy storage technologies and the application potential in power system operation | [19 empty] | Luo et al. (2015). Overview of current development in electrical energy storage technologies and the application potential in power system operation
| 5 | TNO 2018. Ondergrondse Opslag in Nederland: Technische Verkenning | [19 empty] | TNO 2018. Ondergrondse Opslag in Nederland: Technische Verkenning
| 6 | IRENA 2015. Renewables and Electricity Storage: a technology roadmap for REmap 2030 | [19 empty] | IRENA 2015. Renewables and Electricity Storage: a technology roadmap for REmap 2030
| 7 | IEA-ETSAP & IRENA 2012. Electricity storage technology brief | [19 empty] | IEA-ETSAP & IRENA 2012. Electricity storage technology brief
| 8 | FCH JU McKinsey (2015). Commercialisation of energy storage in Europe | [19 empty] | FCH JU McKinsey (2015). Commercialisation of energy storage in Europe
| 9 | Chen et al (2009). Progress in electrical energy storage system: A critical review | [19 empty] | Chen et al (2009). Progress in electrical energy storage system: A critical review
| 10 | Huang et al (2017). Techno-economic modelling of large scale compressed air energy storage systems | [19 empty] | Huang et al (2017). Techno-economic modelling of large scale compressed air energy storage systems
| Others | Add other sources here | [19 empty] | Add other sources here

## ESDL change log (hidden)
November_2022
| Parameter | Old | New | Comment
| Technical lifetime | Various options were stated | 40 | Choice for a value in the middle of the options stated
| Progress ratio | N/A | 1
Rounding (to 3 significant digits)
| Fixed operational costs 2020 | Formula | 0.455
| Fixed operational costs 2030 | Formula | 0.403
| Fixed operational costs 2050 | Formula | 0.338

## Data input (hidden)
FACTSHEET DATA INPUT
Please fill-in here all technology option data including detailed references and sources at the bottom.
TECHNOLOGY DESCRIPTION
| Name of technology option |  | Diabatic compressed air energy storage (CAES) for large-scale temporal electricity storage
| Date of factsheet |  | 2020-02-20
| Sector |  | Electricity generation
Other (specify here)
| ETS / Non-ETS |  | Non-ETS
| Type of Technology |  | Storage
| Description |  | Compressed air energy storage (CAES) is based on storing electricity as compressed air. Compressed air is typically stored underground in suitable geological formations (salt, hard rock and porous rock or aquifer). Aboveground CAES is also a possibility, however investment costs in this case are higher. This factsheet only considers underground CAES whereas air is expanded through a turbine to produce electricity. Diabatic CAES uses fuel (typically natural gas) to heat the expanding air (JRC ETRI, 2014). CAES is typically a large-scale, long-term storage option, and it is applied on the centralised grid. As of 2017, there are two large diabatic CAES projects installed globally, the first one is a 290 MW plant in Germany, and the second one is a 110 MW plant in Alabama, the US (DNV KEMA, 2013; IRENA, 2017). | [17 empty] | Compressed air energy storage (CAES) is based on storing electricity as compressed air. Compressed air is typically stored underground in suitable geological formations (salt, hard rock and porous rock or aquifer). Aboveground CAES is also a possibility, however investment costs in this case are higher. This factsheet only considers underground CAES whereas air is expanded through a turbine to produce electricity. Diabatic CAES uses fuel (typically natural gas) to heat the expanding air (JRC ETRI, 2014). CAES is typically a large-scale, long-term storage option, and it is applied on the centralised grid. As of 2017, there are two large diabatic CAES projects installed globally, the first one is a 290 MW plant in Germany, and the second one is a 110 MW plant in Alabama, the US (DNV KEMA, 2013; IRENA, 2017).
| TRL level 2020 |  | TRL 9
|  |  | The two large existing projects were already installed in 1978 (Germany) and in 1991 (Alabama) (DNV KEMA, 2013). More plants are being prepared, such as a plant in Larne, Ireland (TNO, 2018). | [17 empty] | The two large existing projects were already installed in 1978 (Germany) and in 1991 (Alabama) (DNV KEMA, 2013). More plants are being prepared, such as a plant in Larne, Ireland (TNO, 2018).
TECHNICAL DIMENSIONS
| Factsheet Functional Unit |  | kWh
|  |  | Functional Unit |  |  | Main Source | Source 2 | Source 3 | Source 4 | Source 5
| Capacity |  | kWh |  |  | 3000000 | 580000 | 2860000
[6 empty] | JRC ETRI 2014 | Luo et al. 2015 | Luo et al. 2015 | Reference | Reference
|  |  | Context |  | Unit | 2020 (Current) |  |  |  |  | 2030 |  |  |  |  | 2050
| Potential |  | NL |  | GWh | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5
550
[6 empty] | TNO 2018 | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
| Market share |  | Global utility scale electricity storage |  | % | 0.3%
[6 empty] | IRENA 2015 | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
| Capacity utilization factor |  | Specify here (if not specified, value will be 1)
| Full-load running hours per year |  | Specify here
| Unit of Activity |  | PJ/year
| Activity (Cap2Act) (Optional) |  | Specify here
| Technical lifetime (years) |  | 40
| Progress ratio |  | 1
| Hourly profile |  | No
| Explanation |  | Project specifications determine capacity and detailed project design. An example from TNO (2018): 100 MW/2,860 MWh (26h discharge time) with a cavern of 538.000 m3. Assuming charge time is similar to discharge time (26h), then the compressor capacity required will be 350 m3/s. If faster charge times are desired, a larger compressor is required. The potential estimated by TNO is 50% of the theoretical storage potential in onshore salt caverns in the Netherlands. These salt caverns can also be used for natural gas or hydrogen storage and may therefore not be completely available for CAES (TNO, 2018). As of 2015, the global grid-connected CAES capacity is 440 MW (0.3%) and it is the largest installed utility scale storage after pumped hydro. Pumped hydro dominates the large-scale electricity storage market with over 140 GW installed capacity (99.1% of installed capacity) (IRENA, 2015). More projects are under development (TNO, 2018). Reports on lifetime vary from 30 years (IEA-ETSAP & IRENA, 2012), to 40-55 years (JRC ETRI, 2014), and to 20-100 years (IRENA, 2017). | [17 empty] | Project specifications determine capacity and detailed project design. An example from TNO (2018): 100 MW/2,860 MWh (26h discharge time) with a cavern of 538.000 m3. Assuming charge time is similar to discharge time (26h), then the compressor capacity required will be 350 m3/s. If faster charge times are desired, a larger compressor is required. The potential estimated by TNO is 50% of the theoretical storage potential in onshore salt caverns in the Netherlands. These salt caverns can also be used for natural gas or hydrogen storage and may therefore not be completely available for CAES (TNO, 2018). As of 2015, the global grid-connected CAES capacity is 440 MW (0.3%) and it is the largest installed utility scale storage after pumped hydro. Pumped hydro dominates the large-scale electricity storage market with over 140 GW installed capacity (99.1% of installed capacity) (IRENA, 2015). More projects are under development (TNO, 2018). Reports on lifetime vary from 30 years (IEA-ETSAP & IRENA, 2012), to 40-55 years (JRC ETRI, 2014), and to 20-100 years (IRENA, 2017).
COSTS
| Reference year: €2015 - If amounts are expresed in other currencies or in euros of another year (e.g. €2014), the amount has to be converted. See conversion method in 'READ ME' tab. Costs are per unit of output. |  |  |  |  | 2020 (Current) |  |  |  |  | 2030 |  |  |  |  | 2050
[6 empty] | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5
| Investment costs |  | € / | kWh |  | 35 | 46 | 50 | 2 | 40 | 31 | 38 | 40 |  |  | 26
[6 empty] | JRC ETRI 2014 | IRENA 2017 | FCH JU McKinsey 2015 | Chen et al. 2009 | Chen et al. 2009 | JRC ETRI 2014 | IRENA 2017 | FCH JU McKinsey 2015 | Reference | Reference | JRC ETRI 2014 | Reference | Reference | Reference | Reference
| Other costs per year |  | € / | kWh
[6 empty] | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
| Fixed operational costs per year (excl. fuel costs) |  | € / | kWh |  | 0.455 | N/A | 1.01 | N/A | N/A | 0.403 | N/A | 0.8 |  |  | 0.338
[6 empty] | JRC ETRI 2014 | IRENA 2017 | Own calculation based on FCH JU McKinsey 2015 | Chen et al. 2009 | Chen et al. 2009 | JRC ETRI 2014 | IRENA 2017 | FCH JU McKinsey 2015 | Reference | Reference | JRC ETRI 2014 | Reference | Reference | Reference | Reference
| Variable costs per year (exc. Fuel costs) |  | € / | MWh |  | 1.21 | N/A | 30 | N/A | N/A | 1.21 | N/A | 30 |  |  | 1.21
[6 empty] | JRC ETRI 2014 | IRENA 2017 | FCH JU McKinsey 2015 | Chen et al. 2009 | Chen et al. 2009 | JRC ETRI 2014 | IRENA 2017 | FCH JU McKinsey 2015 | Reference | Reference | JRC ETRI 2014 | Reference | Reference | Reference | Reference
| Costs explanation |  | There are significant degrees of freedom in designing (diabetic) CAES system, such as pump size and turbine size which determine in combination with the reservoir size the charge and discharge times and the energy/power ratio. Design choices such as these influence system costs, which means there are relatively large ranges in costs possible. The sources used have been chosen because they are recent publications and include projections up to (at least) 2030. JRC ETRI (2014) is used as primary source because it has the most complete set of data, including CAPEX and FOM/VOM estimates up to 2050. Details of the cost estimates are not, or only shortly, elaborated in these reports, and estimations of investment costs from other sources vary from 2 €/kWh to 500 €/kWh. Data points for the current year (2020) differ per source: 2020 for JRC ETRI (2014), 2016 for IRENA (2017), 2013 for JCH JU McKinsey (2015), and 2009 for Chen et al. (2009). The main FOM costs calculated using the JRC ETRI (2014) assumption that they represent 1.3% of investment costs. It is assumed that FOM costs remain 1.3% of investment costs in 2020, 2030 and 2050. Other FOM costs are from FCH JU Mckinsey (2015) that states FOM costs as 15 €/kW/year in 2013 and 12 €/kW/year in 2030. These have been calculated to M€/GWh/year assuming a standard storage capacity of 15 hours (200MW/3000MWh system - JRC ETRI, 2014). VOM costs are only provided for 2013 by JRC ETRI (2014) and it is assumed the they remain the same in 2020, 2030 and 2050. VOM costs are defined by JRC ETRI (2014) as production-related O&M costs that vary with electrical generation. They exclude personnel, fuel, and CO2 costs. | [18 empty] | There are significant degrees of freedom in designing (diabetic) CAES system, such as pump size and turbine size which determine in combination with the reservoir size the charge and discharge times and the energy/power ratio. Design choices such as these influence system costs, which means there are relatively large ranges in costs possible. The sources used have been chosen because they are recent publications and include projections up to (at least) 2030. JRC ETRI (2014) is used as primary source because it has the most complete set of data, including CAPEX and FOM/VOM estimates up to 2050. Details of the cost estimates are not, or only shortly, elaborated in these reports, and estimations of investment costs from other sources vary from 2 €/kWh to 500 €/kWh. Data points for the current year (2020) differ per source: 2020 for JRC ETRI (2014), 2016 for IRENA (2017), 2013 for JCH JU McKinsey (2015), and 2009 for Chen et al. (2009). The main FOM costs calculated using the JRC ETRI (2014) assumption that they represent 1.3% of investment costs. It is assumed that FOM costs remain 1.3% of investment costs in 2020, 2030 and 2050. Other FOM costs are from FCH JU Mckinsey (2015) that states FOM costs as 15 €/kW/year in 2013 and 12 €/kW/year in 2030. These have been calculated to M€/GWh/year assuming a standard storage capacity of 15 hours (200MW/3000MWh system - JRC ETRI, 2014). VOM costs are only provided for 2013 by JRC ETRI (2014) and it is assumed the they remain the same in 2020, 2030 and 2050. VOM costs are defined by JRC ETRI (2014) as production-related O&M costs that vary with electrical generation. They exclude personnel, fuel, and CO2 costs.
ENERGY IN- AND OUTPUTS
| Values expressed as a ratio per unit of main output. Inputs as positive and outputs as negative. |  | Energy carrier |  | Unit | 2020 (Current) |  |  |  |  | 2030 |  |  |  |  | 2050
[6 empty] | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5
| Energy carriers (per unit of main output) |  | Electricity |  | PJ | -1
[6 empty] | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
|  |  | Electricity |  | PJ | 0.77
[6 empty] | Calculated based on Huang et al 2017 | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
|  |  | Natural gas |  | PJ | 1.13
[6 empty] | Calculated based on Huang et al 2017 | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
|  |  | Please select |  | PJ
[6 empty] | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
| Energy in- and Outputs explanation |  | The required amounts of electricity and natural gas are stated to obtain 1 PJ of electrical output - based on Huang et al (2017). Note that the output of electricity is higher than the input due to the addition of heat from the combustion of natural gas. Total efficiency is 53% in this configuration, which is at the high end of the 42-54% range reported by DNV KEMA (2013). | [18 empty] | The required amounts of electricity and natural gas are stated to obtain 1 PJ of electrical output - based on Huang et al (2017). Note that the output of electricity is higher than the input due to the addition of heat from the combustion of natural gas. Total efficiency is 53% in this configuration, which is at the high end of the 42-54% range reported by DNV KEMA (2013).
MATERIAL FLOWS (OPTIONAL)
| Material flows |  | Material |  | Unit | 2020 (Current) |  |  |  |  | 2030 |  |  |  |  | 2050
[6 empty] | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5
|  |  | Specify here |  | Specify here
[6 empty] | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
|  |  | Specify here |  | Specify here
[6 empty] | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
| Material flows explanation |  | Explain here | [18 empty] | Explain here
EMISSIONS (Non-fuel/energy-related emissions or emissions reductions (e.g. CCS)
| Emissions |  | Substance |  | Unit | 2020 (Current) |  |  |  |  | 2030 |  |  |  |  | 2050
[6 empty] | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5
|  |  | Please select |  | Please select
[6 empty] | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
|  |  | Please select |  | Please select
[6 empty] | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
|  |  | Please select |  | Please select
[6 empty] | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
|  |  | Please select |  | Please select
[6 empty] | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
| Emissions explanation |  | Explain here (e.g. emission factors if calculated) | [18 empty] | Explain here (e.g. emission factors if calculated)
OTHER
| Specify below the other relevant parameters for the specific technology |  | Unit |  |  | 2020 (Current) |  |  |  |  | 2030 |  |  |  |  | 2050
[6 empty] | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5
| Depth of discharge |  | % |  |  | N/A
[6 empty] | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
| Charge time |  | Hours |  |  | 26
[6 empty] | TNO 2018 | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
| Discharge time |  | Hours |  |  | 15 | 2 | 6 | 26
[6 empty] | Based on JRC ETRI 2014 | TNO 2018 | TNO 2018 | TNO 2018 | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
| Self discharge |  | % / month |  |  | 0
[6 empty] | DNV-KEMA 2013 | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
| Explanation |  | Charge and discharge times are project dependent (see explanation in technical dimensions section). JRC ETRI (2014) states that the minimum time necessary to charge a unit is approximately 8 minutes. TNO (2018) gives the example of 26 hours charge time as stated above. The main discharge time is based on the size of typical system as reported by JRC ETRI (2014) - 200MW/3,000MWh. TNO (2018) compares three plants (Huntdorf (DE), McIntosh (US), and Larne (IE)) with varying specifications (Huntdorf capacity is ca. 300 MW and 600 MWh and McIntosh capacity is ca. 110 MW and 2,860 MWh). Capacity, charge time, and discharge time depend, amongst other things, on cavern size and the specifications of the turbine and compressor used for the project.
REFERENCES AND SOURCES
| 1 | JRC 2014. Energy Technology Reference Indicators (ETRI) projections for 2010-2050 | [19 empty] | JRC 2014. Energy Technology Reference Indicators (ETRI) projections for 2010-2050
| 2 | DNV-KEMA 2013. Systems Analysis Power to Gas (deliverable 1: Technology review) | [19 empty] | DNV-KEMA 2013. Systems Analysis Power to Gas (deliverable 1: Technology review)
| 3 | IRENA 2017. Electricity Storage Costs | [19 empty] | IRENA 2017. Electricity Storage Costs
| 4 | Luo et al. (2015). Overview of current development in electrical energy storage technologies and the application potential in power system operation | [19 empty] | Luo et al. (2015). Overview of current development in electrical energy storage technologies and the application potential in power system operation
| 5 | TNO 2018. Ondergrondse Opslag in Nederland: Technische Verkenning | [19 empty] | TNO 2018. Ondergrondse Opslag in Nederland: Technische Verkenning
| 6 | IRENA 2015. Renewables and Electricity Storage: a technology roadmap for REmap 2030 | [19 empty] | IRENA 2015. Renewables and Electricity Storage: a technology roadmap for REmap 2030
| 7 | IEA-ETSAP & IRENA 2012. Electricity storage technology brief | [19 empty] | IEA-ETSAP & IRENA 2012. Electricity storage technology brief
| 8 | FCH JU McKinsey (2015). Commercialisation of energy storage in Europe | [19 empty] | FCH JU McKinsey (2015). Commercialisation of energy storage in Europe
| 9 | Chen et al (2009). Progress in electrical energy storage system: A critical review | [19 empty] | Chen et al (2009). Progress in electrical energy storage system: A critical review
| 10 | Huang et al (2017). Techno-economic modelling of large scale compressed air energy storage systems | [19 empty] | Huang et al (2017). Techno-economic modelling of large scale compressed air energy storage systems
| Others | Add other sources here | [19 empty] | Add other sources here

## Technology Factsheet
TECHNOLOGY FACTSHEET
v.2
DIABATIC COMPRESSED AIR ENERGY STORAGE (CAES) FOR LARGE-SCALE TEMPORAL ELECTRICITY STORAGE
Date of factsheet | 2020-02-20
Author | Sam Lamboo
Sector | Electricity generation
ETS / Non-ETS | Non-ETS
Type of Technology | Storage
Description | Compressed air energy storage (CAES) is based on storing electricity as compressed air. Compressed air is typically stored underground in suitable geological formations (salt, hard rock and porous rock or aquifer). Aboveground CAES is also a possibility, however investment costs in this case are higher. This factsheet only considers underground CAES whereas air is expanded through a turbine to produce electricity. Diabatic CAES uses fuel (typically natural gas) to heat the expanding air (JRC ETRI, 2014). CAES is typically a large-scale, long-term storage option, and it is applied on the centralised grid. As of 2017, there are two large diabatic CAES projects installed globally, the first one is a 290 MW plant in Germany, and the second one is a 110 MW plant in Alabama, the US (DNV KEMA, 2013; IRENA, 2017). | [11 empty] | Compressed air energy storage (CAES) is based on storing electricity as compressed air. Compressed air is typically stored underground in suitable geological formations (salt, hard rock and porous rock or aquifer). Aboveground CAES is also a possibility, however investment costs in this case are higher. This factsheet only considers underground CAES whereas air is expanded through a turbine to produce electricity. Diabatic CAES uses fuel (typically natural gas) to heat the expanding air (JRC ETRI, 2014). CAES is typically a large-scale, long-term storage option, and it is applied on the centralised grid. As of 2017, there are two large diabatic CAES projects installed globally, the first one is a 290 MW plant in Germany, and the second one is a 110 MW plant in Alabama, the US (DNV KEMA, 2013; IRENA, 2017).
TRL level 2020 | TRL 9
| The two large existing projects were already installed in 1978 (Germany) and in 1991 (Alabama) (DNV KEMA, 2013). More plants are being prepared, such as a plant in Larne, Ireland (TNO, 2018). | [11 empty] | The two large existing projects were already installed in 1978 (Germany) and in 1991 (Alabama) (DNV KEMA, 2013). More plants are being prepared, such as a plant in Larne, Ireland (TNO, 2018).
TECHNICAL DIMENSIONS
| Functional Unit |  |  | Value and Range
Capacity | kWh |  |  | 3000000
|  |  |  | 580000 |  |  | - |  |  | 3000000
| NL |  | GWh | Current |  |  | 2030 |  |  | 2050
Potential |  |  |  | 550 |  |  | 0 |  |  | 0
|  |  |  | Min | − | Max | Min | − | Max | Min | − | Max
Market share | Global utility scale electricity storage |  | % | 0.3% |  |  | 0 |  |  | 0
|  |  |  | Min | − | Max | Min | − | Max | Min | − | Max
Capacity utlization factor | 1
Full-load running hours per year
Unit of Activity | PJ/year
Technical lifetime (years) | 40
Progress ratio | 1
Hourly profile | No
Explanation | Project specifications determine capacity and detailed project design. An example from TNO (2018): 100 MW/2,860 MWh (26h discharge time) with a cavern of 538.000 m3. Assuming charge time is similar to discharge time (26h), then the compressor capacity required will be 350 m3/s. If faster charge times are desired, a larger compressor is required. The potential estimated by TNO is 50% of the theoretical storage potential in onshore salt caverns in the Netherlands. These salt caverns can also be used for natural gas or hydrogen storage and may therefore not be completely available for CAES (TNO, 2018). As of 2015, the global grid-connected CAES capacity is 440 MW (0.3%) and it is the largest installed utility scale storage after pumped hydro. Pumped hydro dominates the large-scale electricity storage market with over 140 GW installed capacity (99.1% of installed capacity) (IRENA, 2015). More projects are under development (TNO, 2018). Reports on lifetime vary from 30 years (IEA-ETSAP & IRENA, 2012), to 40-55 years (JRC ETRI, 2014), and to 20-100 years (IRENA, 2017). | [11 empty] | Project specifications determine capacity and detailed project design. An example from TNO (2018): 100 MW/2,860 MWh (26h discharge time) with a cavern of 538.000 m3. Assuming charge time is similar to discharge time (26h), then the compressor capacity required will be 350 m3/s. If faster charge times are desired, a larger compressor is required. The potential estimated by TNO is 50% of the theoretical storage potential in onshore salt caverns in the Netherlands. These salt caverns can also be used for natural gas or hydrogen storage and may therefore not be completely available for CAES (TNO, 2018). As of 2015, the global grid-connected CAES capacity is 440 MW (0.3%) and it is the largest installed utility scale storage after pumped hydro. Pumped hydro dominates the large-scale electricity storage market with over 140 GW installed capacity (99.1% of installed capacity) (IRENA, 2015). More projects are under development (TNO, 2018). Reports on lifetime vary from 30 years (IEA-ETSAP & IRENA, 2012), to 40-55 years (JRC ETRI, 2014), and to 20-100 years (IRENA, 2017).
COSTS
Year of Euro | 2015
Investment costs | Euro per Functional Unit |  |  | Current |  |  | 2030 |  |  | 2050
| € / | kWh |  | 35 |  |  | 31 |  |  | 26
|  |  |  | 2 | − | 50 | 31 | − | 40 | 26 | − | 26
Other costs per year | € / | kWh |  | 0 |  |  | 0 |  |  | 0
|  |  |  | Min | − | Max | Min | − | Max | Min | − | Max
Fixed operational costs per year (excl. fuel costs) | € / | kWh |  | 0.455 |  |  | 0.403 |  |  | 0.338
|  |  |  | 0.455 | − | 1.01 | 0.403 | − | 0.8 | 0.338 | − | 0.338
Variable costs per year | € / | MWh |  | 1.21 |  |  | 1.21 |  |  | 1.21
|  |  |  | 1.21 | − | 30 | 1.21 | − | 30 | 1.21 | − | 1.21
Costs explanation | There are significant degrees of freedom in designing (diabetic) CAES system, such as pump size and turbine size which determine in combination with the reservoir size the charge and discharge times and the energy/power ratio. Design choices such as these influence system costs, which means there are relatively large ranges in costs possible. The sources used have been chosen because they are recent publications and include projections up to (at least) 2030. JRC ETRI (2014) is used as primary source because it has the most complete set of data, including CAPEX and FOM/VOM estimates up to 2050. Details of the cost estimates are not, or only shortly, elaborated in these reports, and estimations of investment costs from other sources vary from 2 €/kWh to 500 €/kWh. Data points for the current year (2020) differ per source: 2020 for JRC ETRI (2014), 2016 for IRENA (2017), 2013 for JCH JU McKinsey (2015), and 2009 for Chen et al. (2009). The main FOM costs calculated using the JRC ETRI (2014) assumption that they represent 1.3% of investment costs. It is assumed that FOM costs remain 1.3% of investment costs in 2020, 2030 and 2050. Other FOM costs are from FCH JU Mckinsey (2015) that states FOM costs as 15 €/kW/year in 2013 and 12 €/kW/year in 2030. These have been calculated to M€/GWh/year assuming a standard storage capacity of 15 hours (200MW/3000MWh system - JRC ETRI, 2014). VOM costs are only provided for 2013 by JRC ETRI (2014) and it is assumed the they remain the same in 2020, 2030 and 2050. VOM costs are defined by JRC ETRI (2014) as production-related O&M costs that vary with electrical generation. They exclude personnel, fuel, and CO2 costs. | [11 empty] | There are significant degrees of freedom in designing (diabetic) CAES system, such as pump size and turbine size which determine in combination with the reservoir size the charge and discharge times and the energy/power ratio. Design choices such as these influence system costs, which means there are relatively large ranges in costs possible. The sources used have been chosen because they are recent publications and include projections up to (at least) 2030. JRC ETRI (2014) is used as primary source because it has the most complete set of data, including CAPEX and FOM/VOM estimates up to 2050. Details of the cost estimates are not, or only shortly, elaborated in these reports, and estimations of investment costs from other sources vary from 2 €/kWh to 500 €/kWh. Data points for the current year (2020) differ per source: 2020 for JRC ETRI (2014), 2016 for IRENA (2017), 2013 for JCH JU McKinsey (2015), and 2009 for Chen et al. (2009). The main FOM costs calculated using the JRC ETRI (2014) assumption that they represent 1.3% of investment costs. It is assumed that FOM costs remain 1.3% of investment costs in 2020, 2030 and 2050. Other FOM costs are from FCH JU Mckinsey (2015) that states FOM costs as 15 €/kW/year in 2013 and 12 €/kW/year in 2030. These have been calculated to M€/GWh/year assuming a standard storage capacity of 15 hours (200MW/3000MWh system - JRC ETRI, 2014). VOM costs are only provided for 2013 by JRC ETRI (2014) and it is assumed the they remain the same in 2020, 2030 and 2050. VOM costs are defined by JRC ETRI (2014) as production-related O&M costs that vary with electrical generation. They exclude personnel, fuel, and CO2 costs.
ENERGY IN- AND OUTPUTS
Energy carriers (per unit of main output) | Energy carrier |  | Unit | Current |  |  | 2030 |  |  | 2050
| Main output: |  | PJ | -1 |  |  | 0 |  |  | 0
| Electricity |  |  | -1 | − | -1 | Min | − | Max | Min | − | Max
| Electricity |  | PJ | 0.77 |  |  | 0 |  |  | 0
|  |  |  | 0.77 | − | 0.77 | Min | − | Max | Min | − | Max
| Natural gas |  | PJ | 1.13 |  |  | 0 |  |  | 0
|  |  |  | 1.13 | − | 1.13 | Min | − | Max | Min | − | Max
|  |  | PJ | 0 |  |  | 0 |  |  | 0
|  |  |  | Min | − | Max | Min | − | Max | Min | − | Max
Energy in- and Outputs explanation | The required amounts of electricity and natural gas are stated to obtain 1 PJ of electrical output - based on Huang et al (2017). Note that the output of electricity is higher than the input due to the addition of heat from the combustion of natural gas. Total efficiency is 53% in this configuration, which is at the high end of the 42-54% range reported by DNV KEMA (2013). | [11 empty] | The required amounts of electricity and natural gas are stated to obtain 1 PJ of electrical output - based on Huang et al (2017). Note that the output of electricity is higher than the input due to the addition of heat from the combustion of natural gas. Total efficiency is 53% in this configuration, which is at the high end of the 42-54% range reported by DNV KEMA (2013).
EMISSIONS (Non-fuel/energy-related emissions or emissions reductions (e.g. CCS)
Emissions | Substance |  | Unit | Current |  |  | 2030 |  |  | 2050
|  |  |  | 0 |  |  | 0 |  |  | 0
|  |  |  | Min | − | Max | Min | − | Max | Min | − | Max
|  |  |  | 0 |  |  | 0 |  |  | 0
|  |  |  | Min | − | Max | Min | − | Max | Min | − | Max
|  |  |  | 0 |  |  | 0 |  |  | 0
|  |  |  | Min | − | Max | Min | − | Max | Min | − | Max
|  |  |  | 0 |  |  | 0 |  |  | 0
|  |  |  | Min | − | Max | Min | − | Max | Min | − | Max
Emissions explanation
OTHER
Parameter | Unit |  |  | Current |  |  | 2030 |  |  | 2050
Depth of discharge | % |  |  | N/A |  |  | 0 |  |  | 0
|  |  |  | 0 | − | 0 | Min | − | Max | Min | − | Max
Charge time | Hours |  |  | 26 |  |  | 0 |  |  | 0
|  |  |  | 26 | − | 26 | Min | − | Max | Min | − | Max
Discharge time | Hours |  |  | 15 |  |  | 0 |  |  | 0
|  |  |  | 2 | − | 26 | Min | − | Max | Min | − | Max
Self discharge | % / month |  |  | 0 |  |  | 0 |  |  | 0
|  |  |  | 0 | − | 0 | Min | − | Max | Min | − | Max
Explanation | Charge and discharge times are project dependent (see explanation in technical dimensions section). JRC ETRI (2014) states that the minimum time necessary to charge a unit is approximately 8 minutes. TNO (2018) gives the example of 26 hours charge time as stated above. The main discharge time is based on the size of typical system as reported by JRC ETRI (2014) - 200MW/3,000MWh. TNO (2018) compares three plants (Huntdorf (DE), McIntosh (US), and Larne (IE)) with varying specifications (Huntdorf capacity is ca. 300 MW and 600 MWh and McIntosh capacity is ca. 110 MW and 2,860 MWh). Capacity, charge time, and discharge time depend, amongst other things, on cavern size and the specifications of the turbine and compressor used for the project. | [11 empty] | Charge and discharge times are project dependent (see explanation in technical dimensions section). JRC ETRI (2014) states that the minimum time necessary to charge a unit is approximately 8 minutes. TNO (2018) gives the example of 26 hours charge time as stated above. The main discharge time is based on the size of typical system as reported by JRC ETRI (2014) - 200MW/3,000MWh. TNO (2018) compares three plants (Huntdorf (DE), McIntosh (US), and Larne (IE)) with varying specifications (Huntdorf capacity is ca. 300 MW and 600 MWh and McIntosh capacity is ca. 110 MW and 2,860 MWh). Capacity, charge time, and discharge time depend, amongst other things, on cavern size and the specifications of the turbine and compressor used for the project.
REFERENCES AND SOURCES
JRC 2014. Energy Technology Reference Indicators (ETRI) projections for 2010-2050 | [12 empty] | JRC 2014. Energy Technology Reference Indicators (ETRI) projections for 2010-2050
DNV-KEMA 2013. Systems Analysis Power to Gas (deliverable 1: Technology review) | [12 empty] | DNV-KEMA 2013. Systems Analysis Power to Gas (deliverable 1: Technology review)
IRENA 2017. Electricity Storage Costs | [12 empty] | IRENA 2017. Electricity Storage Costs
Luo et al. (2015). Overview of current development in electrical energy storage technologies and the application potential in power system operation | [12 empty] | Luo et al. (2015). Overview of current development in electrical energy storage technologies and the application potential in power system operation
TNO 2018. Ondergrondse Opslag in Nederland: Technische Verkenning | [12 empty] | TNO 2018. Ondergrondse Opslag in Nederland: Technische Verkenning
IRENA 2015. Renewables and Electricity Storage: a technology roadmap for REmap 2030 | [12 empty] | IRENA 2015. Renewables and Electricity Storage: a technology roadmap for REmap 2030
IEA-ETSAP & IRENA 2012. Electricity storage technology brief | [12 empty] | IEA-ETSAP & IRENA 2012. Electricity storage technology brief
FCH JU McKinsey (2015). Commercialisation of energy storage in Europe | [12 empty] | FCH JU McKinsey (2015). Commercialisation of energy storage in Europe
Chen et al (2009). Progress in electrical energy storage system: A critical review | [12 empty] | Chen et al (2009). Progress in electrical energy storage system: A critical review
Huang et al (2017). Techno-economic modelling of large scale compressed air energy storage systems | [12 empty] | Huang et al (2017). Techno-economic modelling of large scale compressed air energy storage systems

## List (hidden)
| Sectors: |  | Type of Technology: |  | Functional Units Capacity: |  | Functional Units Activity: |  | Variable costs units: | Energy carriers: |  | Energy Carriers Units: |  | Material flows: |  | Emissions: |  | Emissions Units:
[10 empty] | Please select main output here | [8 empty] | Please select
| Please select |  | Please select |  | Please select |  | Please select |  | Please select based on chosen Functional Unit | Please select |  | Please select |  | Please select |  | Please select |  | Please select | ETS
| Agriculture: Horticulture |  | Biomass |  | GWe |  | Bln vehicle - km/year |  | MWh | Ambient heat |  | PJ |  |  |  | CH4 |  | kton | Non-ETS
| Agriculture: Other |  | CCS |  | MW |  | PJ/year |  | PJ | Biobenzine | Add here -> |  | Add here -> |  |  | CO2 |  | Mton
| Electricity generation |  | Emission reduction |  | kton |  | kton/year |  | kWh | Biodiesel | Add here -> |  | Add here -> |  |  | F-gassen |  | Mton CO2-eq | Please select
| Gas supply |  | Energy saving |  | Mton |  | Mton/year |  |  | Biofuels | Add here -> |  | Add here -> |  |  | N2O | Add here -> |  | Yes
| Households |  | Renewable |  | Mton ethene |  | Mton ethene/year |  |  | Biofuels FT | Add here -> |  | Add here -> |  |  | Fijn stof PM10 | Add here -> |  | No
| Hydrogen |  | CHP |  | Mton NH3 |  | Mton NH3/year |  |  | Biogas | Add here -> |  | Add here -> |  |  | Fijn stof PM2,5 | Add here ->
| Industry: Anorganic chemics |  | Network |  | Mton steel |  | Mton steel/year |  |  | Bio-LPG |  |  | Add here -> |  |  | SO2 | Add here -> |  | Please select the region
| Industry: Chemics |  | Storage |  | Mvtg | Add here -> |  |  |  | Biomass (coferment) |  |  | Add here -> |  |  | NH3 | Add here -> |  | NL
| Industry: Construction |  | Electrolysis |  | PJ | Add here -> |  |  |  | Biomass (GFT & VGI) |  |  | Add here -> |  |  | NMVOS |  |  | EU
| Industry: Fertiliser | Add here -> |  |  | MWth | Add here -> |  |  |  | Biomass (high quality) |  |  | Add here -> |  |  | NOx |  |  | Global
| Industry: Generic | Add here -> |  | Add here -> | MWh | Add here -> |  |  |  | Biomass (manure) |  |  |  |  | Add here ->
| Industry: Iron and steel | Add here -> |  | Add here -> | GWh | Add here -> |  |  |  | Biomass (starch) |  |  |  |  | Add here -> |  |  |  | mln. € /
| Industry: Non ETS | Add here -> |  | Add here -> | kWh |  |  |  |  | Biomass (sugars) |  |  |  |  | Add here -> |  |  |  | € /
| Industry: Petrochemics | Add here -> |  | Add here -> | [5 empty] | Biomass (waste biogenic) |  |  |  |  | Add here ->
| Mobile machinery |  |  | Add here -> | [5 empty] | Biomass (wet streams) |  |  |  |  | Add here ->
| Refineries | [8 empty] | Biomass (wood abroad)
| Trade, services and utilities | [8 empty] | Biomass (wood interior)
| Transport | [8 empty] | Biomass (wood)
| CCS | [8 empty] | Bio-waste gases
Add here -> | [9 empty] | Blast furnace gas
Add here -> | [9 empty] | CCF gas
Add here -> | [9 empty] | Chemical residual gas
Add here -> | [9 empty] | Coal
Add here -> | [9 empty] | Coke
Coke oven gas
Coking coal
Diesel
Electricity
Energy content manure
Fermentation gas
Gasoline
Geothermal heat
Heat
Heavy fuel oil
Hydrogen
Import electricity
Injection coal
LPG
Natural gas
Natural gas feedstock
Oil
Oil excluding gases
Oil raw materials
Other bio-oil products
Other oil products
Residual gases
Solar energy
Synthetic fuels
Uranium
Waste (non-biogenic)
Wind energy
[8 empty] | Add here -> |  | Benzine
[8 empty] | Add here -> |  | Bio-ethanol
[8 empty] | Add here -> |  | Coal excluding gases
[8 empty] | Add here -> |  | Electricity import
[8 empty] | Add here -> |  | Fuel oil
[8 empty] | Add here -> |  | High Pressure Steam
[8 empty] | Add here -> |  | Hydro
[8 empty] | Add here -> |  | Kerosene
[8 empty] | Add here -> |  | Oil feedstock
[8 empty] | Add here -> |  | Oil products
[8 empty] | Add here -> |  | Other gases
[8 empty] | Add here -> |  | Propane
[8 empty] | Add here -> |  | SNG
[8 empty] | Add here -> |  | Steam

## Calculations (hidden)
ADD CALCULATIONS AND OTHER REFERENCES HERE (OPTIONAL)
Please note that the information placed here will not be included in the Technology Factsheet for disclosure, therefore all relevant details and sources used must be specified in the 'Data input' tab.
Potential (current) and market share calculation. Source: IRENA (2015) - Renewables and Electricity Storage: a technology roadmap for REmap 2030
[7 empty] | Technology | Installed capacity | Market share | Market share (excl pumped hydro)
[7 empty] | Pumped-storage hydro | 141799 | 99.12%
[7 empty] | CAES | 440 | 0.3076% | 34.76%
[7 empty] | Sodium sulphur | 401 | 0.2803% | 31.67%
[7 empty] | Lithium-ion | 238 | 0.1664% | 18.8%
[7 empty] | Advanced lead-acid | 80 | 0.05592% | 6.319%
[7 empty] | Redox flow battery* | 46 | 0.03215% | 3.633%
[7 empty] | Nickel-cadmium | 30 | 0.02097% | 2.37%
[7 empty] | Flywheels | 25 | 0.01747% | 1.975%
[7 empty] | Other batteries | 6 | 0.004194% | 0.4739%
*VRB and ZnBr redox flow batteries
Investment costs
| JRC ETRI | CAPEX (M€2013/GWh) | CAPEX (M€2015/GWh) | CAPEX (€2015/kWh)
| 2020 | 35 | 35.1865 | 35.1865
| 2030 | 31.06 | 31.2255 | 31.2255
| 2050 | 26.25 | 26.3899 | 26.3899
| Sense check JRC ETRI | CAPEX (M€2013/GW) | Storage hours | CAPEX (M€2013/GWh) | CAPEX (M€2015/GWh) | CAPEX (€2015/kWh)
| 2020 | 600 | 15 | 40 | 40.2131 | 40.2131
| 2030 | 530 | 15 | 35.3333 | 35.5216 | 35.5216
| 2050 | 450 | 15 | 30 | 30.1598 | 30.1598
Source for CAPEX (€2013/MW): Reference value JRC 2014 - Energy Technology Referency Indicator (ETRI) projections for 2010-2050
Storage hours calculated from typical sizes from JRC ETRI 2014 (200 MW/3000 MWh). Luo et al. (2015) mention the 110 MW plant in Alabama can operate at full power for 26h.
| Conversion factor €2013 to €2015 from: |  | Statistics Netherlands (CBS), “Consumentenprijzen; Europees geharmoniseerde prijsindex 2015=100”
| IRENA | CAPEX (M$2017/GWh) | CAPEX (M€2017/GWh) | CAPEX (M€2015/GWh) | CAPEX (€2015/kWh)
| 2017 | 53 | 46.9027 | 46.2551 | 46.2551
| 2030 | 44 | 38.9381 | 38.4004 | 38.4004
Source: IRENA 2017 - Electricity Storage Costs
| Conversion factor $2017 to €2017 from: |  | https://www.statista.com/statistics/412794/euro-to-u-s-dollar-annual-average-exchange-rate/
| Conversion factor €2017 to €2015 from: |  | Statistics Netherlands (CBS), “Consumentenprijzen; Europees geharmoniseerde prijsindex 2015=100”
| FCH JU McKinsey | CAPEX (M€2013/GWh) | CAPEX (M€2015/GWh) | CAPEX (€2015/kWh)
| 2013 | 50 | 50.2664 | 50.2664
| 2030 | 40 | 40.2131 | 40.2131
Source: FCH JU McKinsey (2015) - Commercialisation of energy storage in Europe
| Conversion factor €2013 to €2015 from: |  | Statistics Netherlands (CBS), “Consumentenprijzen; Europees geharmoniseerde prijsindex 2015=100”
| Chen et al | CAPEX (M$2009/GWh) | CAPEX (M€2009/GWh) | CAPEX (M€2015/GWh) | CAPEX (€2015/kWh)
| 2009 low | 2 | 1.4388 | 1.5909 | 1.5909
| 2009 high | 50 | 35.9712 | 39.7736 | 39.7736
Source: Chen et al (2009) - Progress in electrical energy storage system: A critical review
| Conversion factor $2009 to €2009 from: |  | https://www.statista.com/statistics/412794/euro-to-u-s-dollar-annual-average-exchange-rate/
| Conversion factor €2009 to €2015 from: |  | Statistics Netherlands (CBS), “Consumentenprijzen; Europees geharmoniseerde prijsindex 2015=100”
O&M costs
| FCH JU McKinsey | FOM (€2013/kW/year) | Storage hours | FOM (€2013/kWh/year) | FOM (M€2013/GWh/year) | FOM (M€2015/GWh/year) | FOM (€2015/kWh/year)
| 2013 | 15 | 15 | 1 | 1 | 1.0053 | 1.0053
| 2030 | 12 | 15 | 0.8 | 0.8 | 0.80426 | 0.80426
Source: FCH JU McKinsey (2015) - Commercialisation of energy storage in Europe
Storage hours calculated from typical sizes from JRC ETRI 2014 (200 MW/3000 MWh). Luo et al. (2015) mention the 110 MW plant in Alabama can operate at full power for 26h.
| Conversion factor €2013 to €2015 from: |  | Statistics Netherlands (CBS), “Consumentenprijzen; Europees geharmoniseerde prijsindex 2015=100”
| JRC ETRI | VOM (€2013/MWh) | VOM(€2015/MWh)
| 2020 | 1.2 | 1.2064
| 2030 | 1.2 | 1.2064
| 2050 | 1.2 | 1.2064
Natural gas consumption and emissions |  |  | Average
| Electrical efficiency | 65-75% | 70%
| Round-trip efficiency | 42-54% | 48%
| Losses | 21-23% | 22% | Usually this is natural gas used to heat up the expanded air
Source: DNV KEMA 2013 - Systems Analysis Power to Gas (deliverable 1: Technology review)
For 1 PJ of electrical output the following is requried
| Electrical input | 1.4286 | PJ | 70% efficiency assumed
| Total input | 2.0833 | PJ | 48% efficiency assumed
| Natural gas | 0.65476 | PJ | Difference total input and electrical input
Emissions factor natural gas
| 56.1 | kg/GJ | Source: RVO (2004) - The Netherlands: list of fuels and standard CO2 emissions
| 201.96 | kg/MWh | https://www.rvo.nl/sites/default/files/2013/10/Vreuls%202005%20NL%20Energiedragerlijst%20-%20Update.pdf
| 56.1 | kton/PJ
Huang |  | Techno-economic modelling of large scale compressed air energy storage systems - Huang et al., Energy Procedia 105 (2017)
Data from Table 2 | [8 empty] | Normalize to 1 |  | efficiency
|  | In | 103 | MW | 10.5 | h | 1081.5 | MWh | 0.7725 |  | 52.6%
|  | NG | 1580 | MWh |  |  | 1580 | MWh | 1.1286
|  | Out | 140 | MW | 10 | h | 1400 | MWh | 1
[7 empty] | 0.52602 | RTE
[7 empty] | 1.1286 | NG in/e out
[7 empty] | 0.7725 | e in / e out

## Visual representation (hidden)
ADD VISUAL REPRESENTATION OF TECHNOLOGY HERE (OPTIONAL)
If available, a visual representation of the technology can be placed here (including sources) to complement the technology description.
Please note that the image will be placed in Technology Factsheet to be disclosed, other non-relevant images can be placed in the 'Calculations' tab.

## Change log (hidden)
CHANGE LOG
| Version: | 1.1
| Date: | 2018-11-05
| Updates: | Visual representation
Decimals
mln. Euro/Euro
Variable costs MWh/PJ/kWh
Name of technology option (bigger)
ECN part of TNO logo