## READ ME (hidden)
GENERAL INSTRUCTIONS
● | The technology factsheet contains information about one specific option (e.g. capacity, potential, costs, energy and emission effects and supporting descriptions).
● | The factsheet must be filled-in by the technical experts in the technology field and used as a reference internally (i.e. input for OPERA model) and externally.
● | The data in the technology factsheet is for technology options in The Netherlands and could be used for EU countries.
● | A regular update of technology factsheet is required every 3-5 years.
● | Read carefully the definitions and instructions for each parameter below and fill-in all data in the 'Data input' tab. The data will be automatically allocated in the factsheet (see 'Factsheet' tab).
● | Units and conversion factors are found below.
● | Lists of sectors, units, energy carriers, etc. are found in the 'List' tab.
● | The 'Factsheet' and 'List' tabs are locked. If a change is necessary, please send a request to Silvana Gamboa or Koen Smekens.
| PARAMETER | DEFINITION |  | HOW TO FILL-IN THE FACTSHEET?
| Sector | ● | To which sector the technology belongs to (according to OPERA classification). | ● | Select the sector from the drop-down menu. If the sector is not available in the menu, please specify in the field 'Other'.
|  |  |  | ● | New sectors can be added to the drop-down menu within the tab 'List' upon request.
| ETS / Non-ETS | ● | Indicate if the technology falls within the Emissions Trading Scheme (ETS).
| Type of Technology | ● | Examples: renewable, saving, CCS, biomass, emission reduction, network (e.g. transformer), etc. | ● | Select the type of technology from the drop-down menu. New types of technologies can be added within the tab 'List' upon request.
| Description | ● | Description of the technology, including technology boundaries, components, applications, etc. | ● | The description is limited up to 700 characters.
| TRL | ● | Select the Technology Readiness Level (TRL) for 2020 based on the assessment below: | ● | Please specify data sources in the explanation box.
NASA/DOD Technology Readiness Level
|  | TRL 9 | Actual system 'flight proven' through succesful mission operations
|  | TRL 8 | Actual system completed and 'flight qualified' through test and demonstration
|  | TRL 7 | System prototype demonstration in space environment
|  | TRL 6 | System/subsystem model or prototype demonstration in a relevant environment (ground or space)
|  | TRL 5 | Component and/or breadboard validation in relevant environment
|  | TRL 4 | Component and/or breadboard validation in laboratory environment
|  | TRL 3 | Analytical and experimental critical function and/or characteristic proof-of-concept
|  | TRL 2 | Technology concept and/or application formulated
|  | TRL 1 | Basic principles observed and reported
TECHNICAL DIMENSIONS
| Factsheet Functional Unit | ● | Unit in which the capacity for production of the main output is expressed e.g. Mton or PJ | ● | The Factsheet Functional Unit chosen provides a reference for the other parameters (i.e. capacity) in order to keep consistency through the factsheet.
|  |  |  | ● | Select the functional unit from the drop-down menu. Conversion factors are found at the bottom of this tab (please specify in the explanation box if other conversion factors are used).
| Capacity | ● | The typical technology capacity size or sizes if there is clear size dependent data. | ● | Technologies that differ largely in size (e.g. large and small scale) must be placed in different factsheets.
|  |  |  | ● | Specify the Capacity value and its respective reference from up to 5 different data sources. Please aggregate all sources in the references and sources box at the bottom of 'Data input' tab.
|  |  |  | ● | Data ranges (min,max) will be automatically allocated in the factsheet.
| Potential | ● | How much of the technology option can be installed in The Netherlands or EU? | ● | Specify the Potential value and its respective reference from up to 5 different data sources. Please aggregate all sources in the references and sources box at the bottom of 'Data input' tab.
|  |  |  | ● | Select which region is covered for the potential from the drop-down menu.
| Market share (Deployment share) | ● | Current market share and maximum expected market share in the future (2030 and 2050). | ● | Market share can be optional for some technologies, in that case, please specify the Potential instead or vice-versa.
|  | ● | Only for competing technologies e.g. heat supply appliances for households such as heat pumps with a market share of 80% of the households. | ● | Specify the Market share and its respective reference from up to 5 different data sources. Please aggregate all sources in the references and sources box at the bottom of 'Data input' tab.
| Capacity utilization factor | ● | The capacity utilization factor is the percentage of the total capacity that is actually being utilized e.g. capacity expansion to absorb additional renewable electricity or over-dimensioning. | ● | If the capacity utlization factor is not filled-in, the value will be automatically assigned as one.
| Full-load running hours per year | ● | The typical number of hours that the technology in question operates per year.
| Unit of Activity | ● | Unit of annual production (output) per year | ● | Select the activity unit from the drop-down menu.
| Activity (Cap2Act) (Optional) | ● | Actual annual production (output) per year | ● | Specify the value for Activity.
|  | ● | Activity = Capacity*Load Factor | ● | Only relevant for infrastructure technologies (e.g. the amount of energy per hour that can be delivered)
| Technical lifetime (years) | ● | The total amount of years during which the technology can technically perform/function before it must be replaced.
| Progress ratio | ● | Progress ratio (PR) is the cost reduction factor achieved by a doubling of the cumulative installed capacity of a technology. Learning rate (LR) = 1 – PR The underlying formula is : Ci= α*Ccumi^b Ci = cost of unit i α = constant (cost unit 1) Ccumi = Cumulative capacity at time of unit i b = learning elasticity A doubling of total cumulative capacity reduces specific costs by a factor of 2b. In the usual case where b is negative, 2b (labelled the progress ratio, PR) is between zero and one. The complement of the progress ratio (1-PR) is called the learning rate (LR). A learning elasticity (b) of -0.32, for example, yields a progress ratio of 0.80 and a learning rate of 20%. This means that the specific capital cost of newly installed capacity decreases by 20% for each doubling of total installed capacity. On a double-logarithmic scale, the decrease in costs appears as a straight line.
| Hourly profile | ● | Is there an hourly profile for the technology? | ● | Select YES/NO
COSTS
| Year of Euro | ● | All costs data must be specified as €2015 | ● | If amounts are expresed in other currencies or in euros of another year (e.g. €2016), the amount has to be converted. See Monetary conversions at the bottom of the tab.
| Investment costs | ● | Total investment costs (CAPEX) in euro in 2020, 2030 and 2050 per functional unit (e.g. per MW, per PJ). | ● | Specify the Costs and their respective reference for 2020(current), 2030 and 2050 from up to 5 different data sources. Please aggregate all sources in the references and sources box at the bottom of 'Data input' tab.
|  | ● | The investments costs are in the case of a new application of the technology. This includes purchase costs, construction costs, net equipment costs and installation costs. Excludes indirect costs, design and site-specific costs. | ● | Specify in the costs explanation box what specifically is included in the investment costs.
|  |  |  | ● | The costs should not be annualized. Site-specific costs (greenfield/brownfield), pre-design costs, pre-construction costs, financing costs should be extracted from the total value.
| Other costs | ● | E.g. electricity connection costs, demolition and removal costs of decommissioned installations. | ● | Please specify Other costs within the Costs explanation box.
|  |  |  | ● | Data input same as above.
| Fixed operational costs (excluding fuel costs) | ● | Fixed operational costs are per year. | ● | Data input same as above.
| Variable costs (excluding fuel costs) | ● | Variable costs are per year. | ● | Data input same as above.
ENERGY IN- AND OUTPUTS
| Energy carriers | ● | Input/output of energy carriers per unit of the main output. The technology may consume/produce more than one input/output. | ● | Select the energy carrier from the drop-down menu (please specify the main output first). Other energy carriers can be added within the tab 'List' upon request.
|  | ● | For each technology, the amount of energy input/output to the process have to be filled in. The process may require more than one input e.g. available waste heat streams can be described as energy outputs or captured CO2 can also be seen as an output). | ● | Specify the values in PJ for 2020, 2030 and 2050 with their respective references from up to 5 different data sources. Please aggregate all sources in the references and sources box at the bottom of 'Data input' tab. Values should be expressed as a ratio per unit of main output whereas inputs should be expressed as positive and values for outputs as negative.
|  |  |  | ● | The value should correspond 'per unit of output' (e.g. output of natural gas with 60% efficiency). Explain the details (i.e. efficiency) in the explanation box.
MATERIAL FLOWS (Optional)
| Material flows | ● | Optional except for technologies with activity level associated e.g. iron, steel, ammonia production, ethylene, ethene. | ● | Specify the material flows and units and add the values for 2020, 2030 and 2050 withtheir respective references from up to 5 difference data sources. Please aggregate all sources in the references and sources box at the bottom of 'Data input' tab.
EMISSIONS
| Emissions | ● | Non-fuel/energy-related emissions or emissions reductions (e.g. CCS) | ● | Select the substance and unit from the drop-down menu. Other emissions can be added within the tab 'List' upon request.
|  |  |  | ● | Specify the Emissions for 2020, 2030 and 2050 with their respective references from up to 5 difference data sources. Please aggregate all sources in the references and sources box at the bottom of 'Data input' tab.
OTHER (Optional)
| Other | ● | Extra relevant parameters for specific technologies e.g. charge/discharge time for batteries, efficiency, etc. | ● | Specify the parameter and unit adding more details in the explanations box below the sub- section. Here, you can specify the relevance of this parameter for the specific technology and references.
|  |  |  | ● | You may add one single value in the main reference for 2020 (current) or add values for 2020, 2030 and 2050 with their respective references from up to 5 difference data sources. Please aggregate all sources in the references and sources box at the bottom of 'Data input' tab.
REFERENCES AND SOURCES
| ● | For values: Add references for each value in their 'Reference' cell (i.e. author and year) and aggregate all references with complete description at the bottom of the 'Data input' tab. If more than 10 references, add other sources under 'Others' box.
| ● | For other data: Add all data sources with complete description at the bottom of the 'Data input' tab. You may link these references with text in the explanatory boxes. If more than 10 references, add other sources under 'Others' box.
UNITS
| Bln vehicle - km |  | Use this unit to represent transport technologies
| GWe |  | Gigawatt electrical
| kton |  | Kiloton
| Mton |  | Megaton
| Mton ethene |  | Megaton ethene
| Mton NH3 |  | Megaton Ammonia
| Mton steel |  | Megaton steel
| Mvtg |  | Million vehicles
| PJ |  | PetaJoule
CONVERSION FACTORS
| COMMON CONVERSIONS |  | 1 MJ = 106 Joule
1 GJ = 109 Joule
1 TJ = 1012 Joule
1 PJ = 1015 Joule
1 MWh = 3,6 GJ
1 GWh = 3,6 TJ
1 TWh = 3,6 PJ
| OTHER CONVERSIONS |  | The International Energy Agency offers a converter for energy units, you can find the converter in the link below:
https://www.iea.org/statistics/resources/unitconverter/
| MONETARY CONVERSIONS | ● | If amounts are expresed in other currencies or in euros of another year (e.g. €2016), the amount has to be converted.
|  | ● | A standard method to correct for inflation is to use the Harmonised Index of Consumer Prices (HICP) (see below). To convert an amount expressed in €2014 to €2017, it has to be multiplied by a factor (HICP 2017/ HICP 2014) = (101,40/99,79) = 1,016.
Harmonised Index of Consumer Prices (HICP) for the Netherlands:
HICP (2015 =100)
|  | 2010 | 92.05
|  | 2011 | 94.32
|  | 2012 | 96.99
|  | 2013 | 99.47
|  | 2014 | 99.79
|  | 2015 | 100
|  | 2016 | 100.11
|  | 2017 | 101.4
Statistics Netherlands (CBS), “Consumentenprijzen; Europees geharmoniseerde prijsindex 2015=100”

## Data input (old) (hidden)
FACTSHEET DATA INPUT
Please fill-in here all technology option data including detailed references and sources at the bottom.
TECHNOLOGY DESCRIPTION
| Name of technology option |  | Electric industrial boiler
| Date of factsheet |  | 2018-12-21
| Sector |  | Industry: Generic
Other (specify here)
| ETS / Non-ETS |  | ETS
| Type of Technology |  | Electrification
| Description |  | There are several types of commercially available industrial electric boiler systems. The most common are: • Using an electric heating element that acts as a resistance (electric boiler) • Using the conductive and resistive properties of the water itself to carry electric current (electrode boiler) There are also infrared- and induction boilers available, but they are small-scale and not commonly available. Electric boilers and electrode boilers mainly apply to utility-related processes (hot water and steam production). The implementation threshold is perceived as relatively low, as it does not require a complete redesign of primary processes (Berenschot, Matters, Delft, & Matters, 2017). Because of the working principle, electric boilers have lower thermal capacities than electrode boilers. Typical capacities of electric boilers are up to 5 MWe, whereas electrode boilers have capacities from 3 MWe up to 70 MWe. Superheated steam with temperatures of up to 350°C and >70 bar can be produced with commercially available electric/electrode boilers (capacities of up to 70 MWe). Advantages of this technology are the following (Berenschot, Matters, Delft, & Matters, 2017; Berenschot, Delft, & ISPT, Power to products, 2015): • An efficiency of up to 95-99.9% • Robust • Can be used as flexible capacity (at times of low electricity prices or as stand-by capacity for gas-fired boilers). Industrial electric boilers are a drop-in solution for steam production. They are implemented on-site at industrial plants where they heat a fluid (typically water for steam production) and require no primary process alterations (Berenschot, Matters, Delft, & Matters, 2017). Examples of electrode boiler manufactures and suppliers are PARAT, Vapor Power, Vapec, Allmech, Zander & Ingestrom, BVA Electrokessel. Examples of electric element boiler manufacturers and suppliers are PARAT, Vapor Power, AB&Co, Danstoker (Thermax) ATTSU, Lattner. | [17 empty] | There are several types of commercially available industrial electric boiler systems. The most common are: • Using an electric heating element that acts as a resistance (electric boiler) • Using the conductive and resistive properties of the water itself to carry electric current (electrode boiler) There are also infrared- and induction boilers available, but they are small-scale and not commonly available. Electric boilers and electrode boilers mainly apply to utility-related processes (hot water and steam production). The implementation threshold is perceived as relatively low, as it does not require a complete redesign of primary processes (Berenschot, Matters, Delft, & Matters, 2017). Because of the working principle, electric boilers have lower thermal capacities than electrode boilers. Typical capacities of electric boilers are up to 5 MWe, whereas electrode boilers have capacities from 3 MWe up to 70 MWe. Superheated steam with temperatures of up to 350°C and >70 bar can be produced with commercially available electric/electrode boilers (capacities of up to 70 MWe). Advantages of this technology are the following (Berenschot, Matters, Delft, & Matters, 2017; Berenschot, Delft, & ISPT, Power to products, 2015): • An efficiency of up to 95-99.9% • Robust • Can be used as flexible capacity (at times of low electricity prices or as stand-by capacity for gas-fired boilers). Industrial electric boilers are a drop-in solution for steam production. They are implemented on-site at industrial plants where they heat a fluid (typically water for steam production) and require no primary process alterations (Berenschot, Matters, Delft, & Matters, 2017). Examples of electrode boiler manufactures and suppliers are PARAT, Vapor Power, Vapec, Allmech, Zander & Ingestrom, BVA Electrokessel. Examples of electric element boiler manufacturers and suppliers are PARAT, Vapor Power, AB&Co, Danstoker (Thermax) ATTSU, Lattner.
| TRL level 2020 |  | TRL 9
|  |  | Current TRL level is 9, established technology (Berenschot, Matters, Delft, & Matters, 2017). | [17 empty] | Current TRL level is 9, established technology (Berenschot, Matters, Delft, & Matters, 2017).
TECHNICAL DIMENSIONS
| Factsheet Functional Unit |  | MWth
|  |  | Functional Unit |  |  | Main Source | Source 2 | Source 3 | Source 4 | Source 5
| Capacity |  | MWth |  |  | 20 | 70 | 15 | 30
[6 empty] | average of Noothout, P.; de Beer, J.; Quant, M.; Blok, K. (2019) Verkenning uitbreiding SDE+ met industriele opties | Berenschot (2017) Electrification in the Dutch process industry | Wieringa, E. (2015) Financial feasibility of using an electric steam boiler in a mutlifuel steam production set and providing grid flexibility | Berenschot; CE Delft; ISPT (2015) Power to products | Reference
|  |  | Functional Unit |  | Context | 2020 (Current) |  |  |  |  | 2030 |  |  |  |  | 2050
| Potential |  | MWth |  | NL | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5
[8 empty] | Reference | Reference | Reference |  |  | Reference | Reference | Reference |  |  | Reference | Reference | Reference
| Market share |  | % |  | Specify here the market | 0
[6 empty] | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
| Capacity utilization factor |  | 1
| Full-load running hours per year |  | 8760
| Unit of Activity |  | PJ/year
| Activity (Cap2Act) (Optional) |  | 0.031536
| Technical lifetime (years) |  | 15
| Progress ratio |  | Specify here
| Hourly profile |  | Yes
| Explanation |  | Electrode boilers can have a capacity of up to 70 MWe. For smaller units, electric boilers can be used (Berenschot, Matters, Delft, & Matters, 2017). Electric boilers are generally used as flexible capacity. This provides advantages during periods of low electricity prices (e.g. during temporary high contributions of wind energy and solar PV during off-peak hours) (Berenschot, Matters, Delft, & Matters, 2017). It is assumed electric/electrode boilers can be used to supply all of the industrial heat demand between 100⁰C – 200⁰C. Depending on the processes, heat demand of up to 350⁰C can also be supplied. According to VNP (2018), electric boilers have a refurbishment interval of 10 years. And according to Berenschot, Delft, & ISPT, Power to products (2015), electric boilers have a lifetime of 15 years. | [17 empty] | Electrode boilers can have a capacity of up to 70 MWe. For smaller units, electric boilers can be used (Berenschot, Matters, Delft, & Matters, 2017). Electric boilers are generally used as flexible capacity. This provides advantages during periods of low electricity prices (e.g. during temporary high contributions of wind energy and solar PV during off-peak hours) (Berenschot, Matters, Delft, & Matters, 2017). It is assumed electric/electrode boilers can be used to supply all of the industrial heat demand between 100⁰C – 200⁰C. Depending on the processes, heat demand of up to 350⁰C can also be supplied. According to VNP (2018), electric boilers have a refurbishment interval of 10 years. And according to Berenschot, Delft, & ISPT, Power to products (2015), electric boilers have a lifetime of 15 years.
COSTS
| Reference year: €2015 - If amounts are expresed in other currencies or in euros of another year (e.g. €2014), the amount has to be converted. See conversion method in 'READ ME' tab. Costs are per unit of output. |  |  |  |  | 2020 (Current) |  |  |  |  | 2030 |  |  |  |  | 2050
[6 empty] | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5
| Investment costs |  | mln. € / | MWth |  | 0.34848 | 0.50505 | 0.19192 | 0.1 | 0.5
[6 empty] | average of Berenschot (2017) | Berenschot (2017) Electrification in the Dutch process industry | Berenschot (2017) Electrification in the Dutch process industry | Noothout, P.; de Beer, J.; Quant, M.; Blok, K. (2019) Verkenning uitbreiding SDE+ met industriele opties | Noothout, P.; de Beer, J.; Quant, M.; Blok, K. (2019) Verkenning uitbreiding SDE+ met industriele opties | Reference |  | Reference | Reference | Reference | Reference |  | Reference | Reference | Reference
| Other costs per year |  | mln. € / | MWth
[6 empty] | Reference | Reference | Reference | Reference |  | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
| Fixed operational costs per year (excl. fuel costs) |  | mln. € / | MW |  | 0.0011
[6 empty] | (Berenschot, Matters, Delft, & Matters, 2017). | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
| Variable costs per year (exc. Fuel costs) |  | mln. € / | MWh |  | 5e-07
[6 empty] | (Berenschot, Matters, Delft, & Matters, 2017). |  | Reference | Reference | Reference | Reference |  | Reference | Reference | Reference | Reference |  | Reference | Reference | Reference
| Costs explanation |  | The bare equipment cost for an electric element boiler is around 140 €/kWe. The electric element accounts for about 65% of the bare equipment cost, and the control box system for 35% (ECN, 2018). The bare equipment cost for an electrode boiler varies from 17 to 60 €/kWe (Berenschot, Matters, Delft, & Matters, 2017; ECN, 2018), depending on the size of the installation. The total investment cost for an electric or electrode boiler is highly case-specific depending on the additional hardware needed and site-specific changes that have to be made, and it can vary from 100 to 500 €/kW-output (Noothout et al., 2019). The fixed O&M costs for an electric boiler are 1.1 €/kW/year, and the variable O&M costs are 0.5 €/MWh (Berenschot, Matters, Delft, & Matters, 2017). | [18 empty] | The bare equipment cost for an electric element boiler is around 140 €/kWe. The electric element accounts for about 65% of the bare equipment cost, and the control box system for 35% (ECN, 2018). The bare equipment cost for an electrode boiler varies from 17 to 60 €/kWe (Berenschot, Matters, Delft, & Matters, 2017; ECN, 2018), depending on the size of the installation. The total investment cost for an electric or electrode boiler is highly case-specific depending on the additional hardware needed and site-specific changes that have to be made, and it can vary from 100 to 500 €/kW-output (Noothout et al., 2019). The fixed O&M costs for an electric boiler are 1.1 €/kW/year, and the variable O&M costs are 0.5 €/MWh (Berenschot, Matters, Delft, & Matters, 2017).
ENERGY IN- AND OUTPUTS
| Values expressed as a ratio per unit of main output. Inputs as positive and outputs as negative. |  | Energy carrier |  | Unit | 2020 (Current) |  |  |  |  | 2030 |  |  |  |  | 2050
[6 empty] | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5
| Energy carriers (per unit of main output) |  | Steam |  | PJ | -1 | -1
[6 empty] | Berenschot (2017) Electrification in the Dutch process industry | VNP (2018) Decarbonising the steam supply of the Dutch paper and board industry |  | Reference | Reference | Reference |  | Reference | Reference | Reference | Reference |  | Reference | Reference | Reference
|  |  | Electricity |  | PJ | 1.0101 | 1.1111
[6 empty] | Berenschot (2017) Electrification in the Dutch process industry | VNP (2018) Decarbonising the steam supply of the Dutch paper and board industry |  | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
|  |  | Please select |  | PJ
[6 empty] | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
|  |  | Please select |  | PJ
[6 empty] | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
| Energy in- and Outputs explanation |  | Electrode and electric boilers have an efficiency of up to 90% (VNP, 2018) to 99.9% (Berenschot, Matters, Delft, & Matters, 2017). | [18 empty] | Electrode and electric boilers have an efficiency of up to 90% (VNP, 2018) to 99.9% (Berenschot, Matters, Delft, & Matters, 2017).
MATERIAL FLOWS (OPTIONAL)
| Material flows |  | Material |  | Unit | 2020 (Current) |  |  |  |  | 2030 |  |  |  |  | 2050
[6 empty] | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5
|  |  | Steam |  | ton | -1 | -1
[6 empty] | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
|  |  | Water |  | ton | 1 | 1
[6 empty] | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
| Material flows explanation |  | Typically water is used to produce steam. | [18 empty] | Typically water is used to produce steam.
EMISSIONS (Non-fuel/energy-related emissions or emissions reductions (e.g. CCS)
| Emissions |  | Substance |  | Unit | 2020 (Current) |  |  |  |  | 2030 |  |  |  |  | 2050
[6 empty] | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5
Please select
[6 empty] | Reference |  | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
|  |  | Please select |  | Please select
[6 empty] | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
|  |  | Please select |  | Please select
[6 empty] | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
|  |  | Please select |  | Please select
[6 empty] | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
| Emissions explanation |  | Explain here (e.g. emission factors if calculated) | [18 empty] | Explain here (e.g. emission factors if calculated)
OTHER
| Specify below the other relevant parameters for the specific technology |  | Unit |  |  | 2020 (Current) |  |  |  |  | 2030 |  |  |  |  | 2050
[6 empty] | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5
| Add here |  | Specify here
[6 empty] | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
| Add here |  | Specify here
[6 empty] | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
| Add here |  | Specify here
[6 empty] | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
| Add here |  | Specify here
[6 empty] | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
Explanation
REFERENCES AND SOURCES
| 1 | Berenschot (2017). Electrification in the Dutch process industry. | [19 empty] | Berenschot (2017). Electrification in the Dutch process industry.
| 2 | VNP (2018). Decarbonising the steam supply of the Dutch paper and board industry. | [19 empty] | VNP (2018). Decarbonising the steam supply of the Dutch paper and board industry.
| 3 | ECN (2010). Benutting restwarmte, Interne notitie. | [19 empty] | ECN (2010). Benutting restwarmte, Interne notitie.
| 4 | Berenschot, Delft, C., & ISPT (2015). Power to products. | [19 empty] | Berenschot, Delft, C., & ISPT (2015). Power to products.
| 5 | Tennet website at: https://www.tennet.eu/nl/elektriciteitsmarkt/aansluiten-op-het-nederlandse-hoogspanningsnet/kosten-van-een-netaansluiting/ | [19 empty] | Tennet website at: https://www.tennet.eu/nl/elektriciteitsmarkt/aansluiten-op-het-nederlandse-hoogspanningsnet/kosten-van-een-netaansluiting/
| 6 | ECN (2018). ECN databases. | [19 empty] | ECN (2018). ECN databases.
| 7 | Noothout, P.; de Beer, J.; Quant, M.; Blok, K. (2019). Verkenning uitbreiding SDE+ met industriële opties. | [19 empty] | Noothout, P.; de Beer, J.; Quant, M.; Blok, K. (2019). Verkenning uitbreiding SDE+ met industriële opties.
| 8 | [20 empty] | 0
| 9 | [20 empty] | 0
| 10 | [20 empty] | 0
| Others | Add other sources here | [19 empty] | Add other sources here

## ESDL change log (hidden)
November_2022
| Parameter | Old | New | Comment
| Functional unit | MWth | MW | Added text to explanation box that MW is meant to be understood as MWth
Rounding (to 3 significant digits)
| Investment costs 2020 | Formula | 0.505
|  | Formula | 0.348
| Input energy carriers | Formula | 1.01
|  | Formula | 1.11

## Data input (hidden)
FACTSHEET DATA INPUT
Please fill-in here all technology option data including detailed references and sources at the bottom.
TECHNOLOGY DESCRIPTION
| Name of technology option |  | Electric industrial boiler
| Date of factsheet |  | 2018-12-21
| Sector |  | Industry: Generic
Other (specify here)
| ETS / Non-ETS |  | ETS
| Type of Technology |  | Electrification
| Description |  | There are several types of commercially available industrial electric boiler systems. The most common are: • Using an electric heating element that acts as a resistance (electric boiler) • Using the conductive and resistive properties of the water itself to carry electric current (electrode boiler) There are also infrared- and induction boilers available, but they are small-scale and not commonly available. Electric boilers and electrode boilers mainly apply to utility-related processes (hot water and steam production). The implementation threshold is perceived as relatively low, as it does not require a complete redesign of primary processes (Berenschot, Matters, Delft, & Matters, 2017). Because of the working principle, electric boilers have lower thermal capacities than electrode boilers. Typical capacities of electric boilers are up to 5 MWe, whereas electrode boilers have capacities from 3 MWe up to 70 MWe. Superheated steam with temperatures of up to 350°C and >70 bar can be produced with commercially available electric/electrode boilers (capacities of up to 70 MWe). Advantages of this technology are the following (Berenschot, Matters, Delft, & Matters, 2017; Berenschot, Delft, & ISPT, Power to products, 2015): • An efficiency of up to 95-99.9% • Robust • Can be used as flexible capacity (at times of low electricity prices or as stand-by capacity for gas-fired boilers). Industrial electric boilers are a drop-in solution for steam production. They are implemented on-site at industrial plants where they heat a fluid (typically water for steam production) and require no primary process alterations (Berenschot, Matters, Delft, & Matters, 2017). Examples of electrode boiler manufactures and suppliers are PARAT, Vapor Power, Vapec, Allmech, Zander & Ingestrom, BVA Electrokessel. Examples of electric element boiler manufacturers and suppliers are PARAT, Vapor Power, AB&Co, Danstoker (Thermax) ATTSU, Lattner. | [17 empty] | There are several types of commercially available industrial electric boiler systems. The most common are: • Using an electric heating element that acts as a resistance (electric boiler) • Using the conductive and resistive properties of the water itself to carry electric current (electrode boiler) There are also infrared- and induction boilers available, but they are small-scale and not commonly available. Electric boilers and electrode boilers mainly apply to utility-related processes (hot water and steam production). The implementation threshold is perceived as relatively low, as it does not require a complete redesign of primary processes (Berenschot, Matters, Delft, & Matters, 2017). Because of the working principle, electric boilers have lower thermal capacities than electrode boilers. Typical capacities of electric boilers are up to 5 MWe, whereas electrode boilers have capacities from 3 MWe up to 70 MWe. Superheated steam with temperatures of up to 350°C and >70 bar can be produced with commercially available electric/electrode boilers (capacities of up to 70 MWe). Advantages of this technology are the following (Berenschot, Matters, Delft, & Matters, 2017; Berenschot, Delft, & ISPT, Power to products, 2015): • An efficiency of up to 95-99.9% • Robust • Can be used as flexible capacity (at times of low electricity prices or as stand-by capacity for gas-fired boilers). Industrial electric boilers are a drop-in solution for steam production. They are implemented on-site at industrial plants where they heat a fluid (typically water for steam production) and require no primary process alterations (Berenschot, Matters, Delft, & Matters, 2017). Examples of electrode boiler manufactures and suppliers are PARAT, Vapor Power, Vapec, Allmech, Zander & Ingestrom, BVA Electrokessel. Examples of electric element boiler manufacturers and suppliers are PARAT, Vapor Power, AB&Co, Danstoker (Thermax) ATTSU, Lattner.
| TRL level 2020 |  | TRL 9
|  |  | Current TRL level is 9, established technology (Berenschot, Matters, Delft, & Matters, 2017). | [17 empty] | Current TRL level is 9, established technology (Berenschot, Matters, Delft, & Matters, 2017).
TECHNICAL DIMENSIONS
| Factsheet Functional Unit |  | MW
|  |  | Functional Unit |  |  | Main Source | Source 2 | Source 3 | Source 4 | Source 5
| Capacity |  | MW |  |  | 20 | 70 | 15 | 30
[6 empty] | average of Noothout, P.; de Beer, J.; Quant, M.; Blok, K. (2019) Verkenning uitbreiding SDE+ met industriele opties | Berenschot (2017) Electrification in the Dutch process industry | Wieringa, E. (2015) Financial feasibility of using an electric steam boiler in a mutlifuel steam production set and providing grid flexibility | Berenschot; CE Delft; ISPT (2015) Power to products | Reference
|  |  | Functional Unit |  | Context | 2020 (Current) |  |  |  |  | 2030 |  |  |  |  | 2050
| Potential |  | MW |  | NL | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5
[8 empty] | Reference | Reference | Reference |  |  | Reference | Reference | Reference |  |  | Reference | Reference | Reference
| Market share |  | % |  | Specify here the market | 0
[6 empty] | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
| Capacity utilization factor |  | 1
| Full-load running hours per year |  | 8760
| Unit of Activity |  | PJ/year
| Activity (Cap2Act) (Optional) |  | 0.031536
| Technical lifetime (years) |  | 15
| Progress ratio |  | Specify here
| Hourly profile |  | Yes
| Explanation |  | The functional unit MW referes to MWth. Electrode boilers can have a capacity of up to 70 MWe. For smaller units, electric boilers can be used (Berenschot, Matters, Delft, & Matters, 2017). Electric boilers are generally used as flexible capacity. This provides advantages during periods of low electricity prices (e.g. during temporary high contributions of wind energy and solar PV during off-peak hours) (Berenschot, Matters, Delft, & Matters, 2017). It is assumed electric/electrode boilers can be used to supply all of the industrial heat demand between 100⁰C – 200⁰C. Depending on the processes, heat demand of up to 350⁰C can also be supplied. According to VNP (2018), electric boilers have a refurbishment interval of 10 years. And according to Berenschot, Delft, & ISPT, Power to products (2015), electric boilers have a lifetime of 15 years. | [17 empty] | The functional unit MW referes to MWth. Electrode boilers can have a capacity of up to 70 MWe. For smaller units, electric boilers can be used (Berenschot, Matters, Delft, & Matters, 2017). Electric boilers are generally used as flexible capacity. This provides advantages during periods of low electricity prices (e.g. during temporary high contributions of wind energy and solar PV during off-peak hours) (Berenschot, Matters, Delft, & Matters, 2017). It is assumed electric/electrode boilers can be used to supply all of the industrial heat demand between 100⁰C – 200⁰C. Depending on the processes, heat demand of up to 350⁰C can also be supplied. According to VNP (2018), electric boilers have a refurbishment interval of 10 years. And according to Berenschot, Delft, & ISPT, Power to products (2015), electric boilers have a lifetime of 15 years.
COSTS
| Reference year: €2015 - If amounts are expresed in other currencies or in euros of another year (e.g. €2014), the amount has to be converted. See conversion method in 'READ ME' tab. Costs are per unit of output. |  |  |  |  | 2020 (Current) |  |  |  |  | 2030 |  |  |  |  | 2050
[6 empty] | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5
| Investment costs |  | mln. € / | MW |  | 0.348 | 0.505 | 0.19192 | 0.1 | 0.5
[6 empty] | average of Berenschot (2017) | Berenschot (2017) Electrification in the Dutch process industry | Berenschot (2017) Electrification in the Dutch process industry | Noothout, P.; de Beer, J.; Quant, M.; Blok, K. (2019) Verkenning uitbreiding SDE+ met industriele opties | Noothout, P.; de Beer, J.; Quant, M.; Blok, K. (2019) Verkenning uitbreiding SDE+ met industriele opties | Reference |  | Reference | Reference | Reference | Reference |  | Reference | Reference | Reference
| Other costs per year |  | mln. € / | MW
[6 empty] | Reference | Reference | Reference | Reference |  | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
| Fixed operational costs per year (excl. fuel costs) |  | mln. € / | MW |  | 0.0011
[6 empty] | (Berenschot, Matters, Delft, & Matters, 2017). | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
| Variable costs per year (exc. Fuel costs) |  | mln. € / | MWh |  | 5e-07
[6 empty] | (Berenschot, Matters, Delft, & Matters, 2017). |  | Reference | Reference | Reference | Reference |  | Reference | Reference | Reference | Reference |  | Reference | Reference | Reference
| Costs explanation |  | The bare equipment cost for an electric element boiler is around 140 €/kWe. The electric element accounts for about 65% of the bare equipment cost, and the control box system for 35% (ECN, 2018). The bare equipment cost for an electrode boiler varies from 17 to 60 €/kWe (Berenschot, Matters, Delft, & Matters, 2017; ECN, 2018), depending on the size of the installation. The total investment cost for an electric or electrode boiler is highly case-specific depending on the additional hardware needed and site-specific changes that have to be made, and it can vary from 100 to 500 €/kW-output (Noothout et al., 2019). The fixed O&M costs for an electric boiler are 1.1 €/kW/year, and the variable O&M costs are 0.5 €/MWh (Berenschot, Matters, Delft, & Matters, 2017). | [18 empty] | The bare equipment cost for an electric element boiler is around 140 €/kWe. The electric element accounts for about 65% of the bare equipment cost, and the control box system for 35% (ECN, 2018). The bare equipment cost for an electrode boiler varies from 17 to 60 €/kWe (Berenschot, Matters, Delft, & Matters, 2017; ECN, 2018), depending on the size of the installation. The total investment cost for an electric or electrode boiler is highly case-specific depending on the additional hardware needed and site-specific changes that have to be made, and it can vary from 100 to 500 €/kW-output (Noothout et al., 2019). The fixed O&M costs for an electric boiler are 1.1 €/kW/year, and the variable O&M costs are 0.5 €/MWh (Berenschot, Matters, Delft, & Matters, 2017).
ENERGY IN- AND OUTPUTS
| Values expressed as a ratio per unit of main output. Inputs as positive and outputs as negative. |  | Energy carrier |  | Unit | 2020 (Current) |  |  |  |  | 2030 |  |  |  |  | 2050
[6 empty] | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5
| Energy carriers (per unit of main output) |  | Steam |  | PJ | -1 | -1
[6 empty] | Berenschot (2017) Electrification in the Dutch process industry | VNP (2018) Decarbonising the steam supply of the Dutch paper and board industry |  | Reference | Reference | Reference |  | Reference | Reference | Reference | Reference |  | Reference | Reference | Reference
|  |  | Electricity |  | PJ | 1.01 | 1.11
[6 empty] | Berenschot (2017) Electrification in the Dutch process industry | VNP (2018) Decarbonising the steam supply of the Dutch paper and board industry |  | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
|  |  | Please select |  | PJ
[6 empty] | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
|  |  | Please select |  | PJ
[6 empty] | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
| Energy in- and Outputs explanation |  | Electrode and electric boilers have an efficiency of up to 90% (VNP, 2018) to 99.9% (Berenschot, Matters, Delft, & Matters, 2017). | [18 empty] | Electrode and electric boilers have an efficiency of up to 90% (VNP, 2018) to 99.9% (Berenschot, Matters, Delft, & Matters, 2017).
MATERIAL FLOWS (OPTIONAL)
| Material flows |  | Material |  | Unit | 2020 (Current) |  |  |  |  | 2030 |  |  |  |  | 2050
[6 empty] | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5
|  |  | Steam |  | ton | -1 | -1
[6 empty] | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
|  |  | Water |  | ton | 1 | 1
[6 empty] | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
| Material flows explanation |  | Typically water is used to produce steam. | [18 empty] | Typically water is used to produce steam.
EMISSIONS (Non-fuel/energy-related emissions or emissions reductions (e.g. CCS)
| Emissions |  | Substance |  | Unit | 2020 (Current) |  |  |  |  | 2030 |  |  |  |  | 2050
[6 empty] | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5
Please select
[6 empty] | Reference |  | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
|  |  | Please select |  | Please select
[6 empty] | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
|  |  | Please select |  | Please select
[6 empty] | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
|  |  | Please select |  | Please select
[6 empty] | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
| Emissions explanation |  | Explain here (e.g. emission factors if calculated) | [18 empty] | Explain here (e.g. emission factors if calculated)
OTHER
| Specify below the other relevant parameters for the specific technology |  | Unit |  |  | 2020 (Current) |  |  |  |  | 2030 |  |  |  |  | 2050
[6 empty] | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5 | Main Source | Source 2 | Source 3 | Source 4 | Source 5
| Add here |  | Specify here
[6 empty] | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
| Add here |  | Specify here
[6 empty] | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
| Add here |  | Specify here
[6 empty] | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
| Add here |  | Specify here
[6 empty] | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference | Reference
Explanation
REFERENCES AND SOURCES
| 1 | Berenschot (2017). Electrification in the Dutch process industry. | [19 empty] | Berenschot (2017). Electrification in the Dutch process industry.
| 2 | VNP (2018). Decarbonising the steam supply of the Dutch paper and board industry. | [19 empty] | VNP (2018). Decarbonising the steam supply of the Dutch paper and board industry.
| 3 | ECN (2010). Benutting restwarmte, Interne notitie. | [19 empty] | ECN (2010). Benutting restwarmte, Interne notitie.
| 4 | Berenschot, Delft, C., & ISPT (2015). Power to products. | [19 empty] | Berenschot, Delft, C., & ISPT (2015). Power to products.
| 5 | Tennet website at: https://www.tennet.eu/nl/elektriciteitsmarkt/aansluiten-op-het-nederlandse-hoogspanningsnet/kosten-van-een-netaansluiting/ | [19 empty] | Tennet website at: https://www.tennet.eu/nl/elektriciteitsmarkt/aansluiten-op-het-nederlandse-hoogspanningsnet/kosten-van-een-netaansluiting/
| 6 | ECN (2018). ECN databases. | [19 empty] | ECN (2018). ECN databases.
| 7 | Noothout, P.; de Beer, J.; Quant, M.; Blok, K. (2019). Verkenning uitbreiding SDE+ met industriële opties. | [19 empty] | Noothout, P.; de Beer, J.; Quant, M.; Blok, K. (2019). Verkenning uitbreiding SDE+ met industriële opties.
| 8 | [20 empty] | 0
| 9 | [20 empty] | 0
| 10 | [20 empty] | 0
| Others | Add other sources here | [19 empty] | Add other sources here

## Technology Factsheet
TECHNOLOGY FACTSHEET
ELECTRIC INDUSTRIAL BOILER
Date of factsheet | 2018-12-21
Author | Marc Marsidi
Sector | Industry: Generic
ETS / Non-ETS | ETS
Type of Technology | Electrification
Description | There are several types of commercially available industrial electric boiler systems. The most common are: • Using an electric heating element that acts as a resistance (electric boiler) • Using the conductive and resistive properties of the water itself to carry electric current (electrode boiler) There are also infrared- and induction boilers available, but they are small-scale and not commonly available. Electric boilers and electrode boilers mainly apply to utility-related processes (hot water and steam production). The implementation threshold is perceived as relatively low, as it does not require a complete redesign of primary processes (Berenschot, Matters, Delft, & Matters, 2017). Because of the working principle, electric boilers have lower thermal capacities than electrode boilers. Typical capacities of electric boilers are up to 5 MWe, whereas electrode boilers have capacities from 3 MWe up to 70 MWe. Superheated steam with temperatures of up to 350°C and >70 bar can be produced with commercially available electric/electrode boilers (capacities of up to 70 MWe). Advantages of this technology are the following (Berenschot, Matters, Delft, & Matters, 2017; Berenschot, Delft, & ISPT, Power to products, 2015): • An efficiency of up to 95-99.9% • Robust • Can be used as flexible capacity (at times of low electricity prices or as stand-by capacity for gas-fired boilers). Industrial electric boilers are a drop-in solution for steam production. They are implemented on-site at industrial plants where they heat a fluid (typically water for steam production) and require no primary process alterations (Berenschot, Matters, Delft, & Matters, 2017). Examples of electrode boiler manufactures and suppliers are PARAT, Vapor Power, Vapec, Allmech, Zander & Ingestrom, BVA Electrokessel. Examples of electric element boiler manufacturers and suppliers are PARAT, Vapor Power, AB&Co, Danstoker (Thermax) ATTSU, Lattner. | [11 empty] | There are several types of commercially available industrial electric boiler systems. The most common are: • Using an electric heating element that acts as a resistance (electric boiler) • Using the conductive and resistive properties of the water itself to carry electric current (electrode boiler) There are also infrared- and induction boilers available, but they are small-scale and not commonly available. Electric boilers and electrode boilers mainly apply to utility-related processes (hot water and steam production). The implementation threshold is perceived as relatively low, as it does not require a complete redesign of primary processes (Berenschot, Matters, Delft, & Matters, 2017). Because of the working principle, electric boilers have lower thermal capacities than electrode boilers. Typical capacities of electric boilers are up to 5 MWe, whereas electrode boilers have capacities from 3 MWe up to 70 MWe. Superheated steam with temperatures of up to 350°C and >70 bar can be produced with commercially available electric/electrode boilers (capacities of up to 70 MWe). Advantages of this technology are the following (Berenschot, Matters, Delft, & Matters, 2017; Berenschot, Delft, & ISPT, Power to products, 2015): • An efficiency of up to 95-99.9% • Robust • Can be used as flexible capacity (at times of low electricity prices or as stand-by capacity for gas-fired boilers). Industrial electric boilers are a drop-in solution for steam production. They are implemented on-site at industrial plants where they heat a fluid (typically water for steam production) and require no primary process alterations (Berenschot, Matters, Delft, & Matters, 2017). Examples of electrode boiler manufactures and suppliers are PARAT, Vapor Power, Vapec, Allmech, Zander & Ingestrom, BVA Electrokessel. Examples of electric element boiler manufacturers and suppliers are PARAT, Vapor Power, AB&Co, Danstoker (Thermax) ATTSU, Lattner.
TRL level 2020 | TRL 9
| Current TRL level is 9, established technology (Berenschot, Matters, Delft, & Matters, 2017). | [11 empty] | Current TRL level is 9, established technology (Berenschot, Matters, Delft, & Matters, 2017).
TECHNICAL DIMENSIONS
| Functional Unit |  |  | Value and Range
Capacity | MW |  |  | 20
|  |  |  | 15 |  |  | - |  |  | 70
| MW |  | NL | Current |  |  | 2030 |  |  | 2050
Potential |  |  |  | 0 |  |  | 0 |  |  | 0
|  |  |  | Min | - | Max | Min | - | Max | Min | - | Max
Market share | % |  |  | 0 |  |  | 0 |  |  | 0
|  |  |  | 0 | - | 0 | Min | - | Max | Min | - | Max
Capacity utlization factor | 1
Full-load running hours per year | 8760
Unit of Activity | PJ/year | 0.031536
Technical lifetime (years) | 15
Progress ratio
Hourly profile | Yes
Explanation | The functional unit MW referes to MWth. Electrode boilers can have a capacity of up to 70 MWe. For smaller units, electric boilers can be used (Berenschot, Matters, Delft, & Matters, 2017). Electric boilers are generally used as flexible capacity. This provides advantages during periods of low electricity prices (e.g. during temporary high contributions of wind energy and solar PV during off-peak hours) (Berenschot, Matters, Delft, & Matters, 2017). It is assumed electric/electrode boilers can be used to supply all of the industrial heat demand between 100⁰C – 200⁰C. Depending on the processes, heat demand of up to 350⁰C can also be supplied. According to VNP (2018), electric boilers have a refurbishment interval of 10 years. And according to Berenschot, Delft, & ISPT, Power to products (2015), electric boilers have a lifetime of 15 years. | [11 empty] | The functional unit MW referes to MWth. Electrode boilers can have a capacity of up to 70 MWe. For smaller units, electric boilers can be used (Berenschot, Matters, Delft, & Matters, 2017). Electric boilers are generally used as flexible capacity. This provides advantages during periods of low electricity prices (e.g. during temporary high contributions of wind energy and solar PV during off-peak hours) (Berenschot, Matters, Delft, & Matters, 2017). It is assumed electric/electrode boilers can be used to supply all of the industrial heat demand between 100⁰C – 200⁰C. Depending on the processes, heat demand of up to 350⁰C can also be supplied. According to VNP (2018), electric boilers have a refurbishment interval of 10 years. And according to Berenschot, Delft, & ISPT, Power to products (2015), electric boilers have a lifetime of 15 years.
COSTS
Year of Euro | 2015
Investment costs | Euro per Functional Unit |  |  | Current |  |  | 2030 |  |  | 2050
| mln. € / | MW |  | 0.348 |  |  | 0 |  |  | 0
|  |  |  | 0.1 | - | 0.505 | Min | - | Max | Min | - | Max
Other costs per year | mln. € / | MW |  | 0 |  |  | 0 |  |  | 0
|  |  |  | Min | - | Max | Min | - | Max | Min | - | Max
Fixed operational costs per year (excl. fuel costs) | mln. € / | MW |  | 0.0011 |  |  | 0 |  |  | 0
|  |  |  | Min | - | Max | Min | - | Max | Min | - | Max
Variable costs per year | mln. € / | MWh |  | 0 |  |  | 0 |  |  | 0
|  |  |  | Min | - | Max | Min | - | Max | Min | - | Max
Costs explanation | The bare equipment cost for an electric element boiler is around 140 €/kWe. The electric element accounts for about 65% of the bare equipment cost, and the control box system for 35% (ECN, 2018). The bare equipment cost for an electrode boiler varies from 17 to 60 €/kWe (Berenschot, Matters, Delft, & Matters, 2017; ECN, 2018), depending on the size of the installation. The total investment cost for an electric or electrode boiler is highly case-specific depending on the additional hardware needed and site-specific changes that have to be made, and it can vary from 100 to 500 €/kW-output (Noothout et al., 2019). The fixed O&M costs for an electric boiler are 1.1 €/kW/year, and the variable O&M costs are 0.5 €/MWh (Berenschot, Matters, Delft, & Matters, 2017). | [11 empty] | The bare equipment cost for an electric element boiler is around 140 €/kWe. The electric element accounts for about 65% of the bare equipment cost, and the control box system for 35% (ECN, 2018). The bare equipment cost for an electrode boiler varies from 17 to 60 €/kWe (Berenschot, Matters, Delft, & Matters, 2017; ECN, 2018), depending on the size of the installation. The total investment cost for an electric or electrode boiler is highly case-specific depending on the additional hardware needed and site-specific changes that have to be made, and it can vary from 100 to 500 €/kW-output (Noothout et al., 2019). The fixed O&M costs for an electric boiler are 1.1 €/kW/year, and the variable O&M costs are 0.5 €/MWh (Berenschot, Matters, Delft, & Matters, 2017).
ENERGY IN- AND OUTPUTS
Energy carriers (per unit of main output) | Energy carrier |  | Unit | Current |  |  | 2030 |  |  | 2050
| Main output: |  | PJ | -1 |  |  | 0 |  |  | 0
| Steam |  |  | -1 | - | -1 | Min | - | Max | Min | - | Max
| Electricity |  | PJ | 1.01 |  |  | 0 |  |  | 0
|  |  |  | 1.01 | - | 1.11 | Min | - | Max | Min | - | Max
|  |  | PJ | 0 |  |  | 0 |  |  | 0
|  |  |  | Min | - | Max | Min | - | Max | Min | - | Max
|  |  | PJ | 0 |  |  | 0 |  |  | 0
|  |  |  | Min | - | Max | Min | - | Max | Min | - | Max
Energy in- and Outputs explanation | Electrode and electric boilers have an efficiency of up to 90% (VNP, 2018) to 99.9% (Berenschot, Matters, Delft, & Matters, 2017). | [11 empty] | Electrode and electric boilers have an efficiency of up to 90% (VNP, 2018) to 99.9% (Berenschot, Matters, Delft, & Matters, 2017).
MATERIAL FLOWS (OPTIONAL)
Material flows | Material |  | Unit | Current |  |  | 2030 |  |  | 2050
| Steam |  | ton | -1 |  |  | 0 |  |  | 0
|  |  |  | -1 | - | -1 | Min | - | Max | Min | - | Max
| Water |  | ton | 1 |  |  | 0 |  |  | 0
|  |  |  | 1 | - | 1 | Min | - | Max | Min | - | Max
Material flows explanation | Typically water is used to produce steam. | [11 empty] | Typically water is used to produce steam.
EMISSIONS (Non-fuel/energy-related emissions or emissions reductions (e.g. CCS)
Emissions | Substance |  | Unit | Current |  |  | 2030 |  |  | 2050
|  |  |  | 0 |  |  | 0 |  |  | 0
|  |  |  | Min | - | Max | Min | - | Max | Min | - | Max
|  |  |  | 0 |  |  | 0 |  |  | 0
|  |  |  | Min | - | Max | Min | - | Max | Min | - | Max
|  |  |  | 0 |  |  | 0 |  |  | 0
|  |  |  | Min | - | Max | Min | - | Max | Min | - | Max
|  |  |  | 0 |  |  | 0 |  |  | 0
|  |  |  | Min | - | Max | Min | - | Max | Min | - | Max
Emissions explanation
REFERENCES AND SOURCES
Berenschot (2017). Electrification in the Dutch process industry. | [12 empty] | Berenschot (2017). Electrification in the Dutch process industry.
VNP (2018). Decarbonising the steam supply of the Dutch paper and board industry. | [12 empty] | VNP (2018). Decarbonising the steam supply of the Dutch paper and board industry.
ECN (2010). Benutting restwarmte, Interne notitie. | [12 empty] | ECN (2010). Benutting restwarmte, Interne notitie.
Berenschot, Delft, C., & ISPT (2015). Power to products. | [12 empty] | Berenschot, Delft, C., & ISPT (2015). Power to products.
Tennet website at: https://www.tennet.eu/nl/elektriciteitsmarkt/aansluiten-op-het-nederlandse-hoogspanningsnet/kosten-van-een-netaansluiting/ | [12 empty] | Tennet website at: https://www.tennet.eu/nl/elektriciteitsmarkt/aansluiten-op-het-nederlandse-hoogspanningsnet/kosten-van-een-netaansluiting/
ECN (2018). ECN databases. | [12 empty] | ECN (2018). ECN databases.
Noothout, P.; de Beer, J.; Quant, M.; Blok, K. (2019). Verkenning uitbreiding SDE+ met industriële opties. | [12 empty] | Noothout, P.; de Beer, J.; Quant, M.; Blok, K. (2019). Verkenning uitbreiding SDE+ met industriële opties.

## List (hidden)
| Sectors: |  | Type of Technology: |  | Functional Units Capacity: |  | Functional Units Activity: |  | Energy carriers: |  | Energy Carriers Units: |  | Material flows: |  | Emissions: |  | Emissions Units:
[9 empty] | Please select main output here | [8 empty] | Please select
| Please select |  | Please select |  | Please select |  | Please select |  | Please select |  | Please select |  | Please select |  | Please select |  | Please select | ETS
| Agriculture: Horticulture |  | Biomass |  | GWe |  | Bln vehicle - km/year |  | Ambient heat |  | PJ |  |  |  | CH4 |  | kton | Non-ETS
| Agriculture: Other |  | CCS |  | MW |  | PJ/year |  | Biobenzine | Add here -> |  | Add here -> |  |  | CO2 |  | Mton
| Electricity generation |  | Emission reduction |  | kton |  | kton/year |  | Biodiesel | Add here -> |  | Add here -> |  |  | F-gassen |  | Mton CO2-eq | Please select
| Gas supply |  | Energy saving |  | Mton |  | Mton/year |  | Biofuels | Add here -> |  | Add here -> |  |  | N2O | Add here -> |  | Yes
| Households |  | Renewable |  | Mton ethene |  | Mton ethene/year |  | Biofuels FT | Add here -> |  | Add here -> |  |  | Fijn stof PM10 | Add here -> |  | No
| Hydrogen |  | CHP |  | Mton NH3 |  | Mton NH3/year |  | Biogas | Add here -> |  | Add here -> |  |  | Fijn stof PM2,5 | Add here ->
| Industry: Anorganic chemics |  | Network |  | Mton steel |  | Mton steel/year |  | Bio-LPG |  |  | Add here -> |  |  | SO2 | Add here -> |  | Please select the region
| Industry: Chemics |  | Storage |  | Mvtg | Add here -> |  |  | Biomass (coferment) |  |  | Add here -> |  |  | NH3 | Add here -> |  | NL
| Industry: Construction |  | Electrolysis |  | PJ | Add here -> |  |  | Biomass (GFT & VGI) |  |  | Add here -> |  |  | NMVOS |  |  | EU
| Industry: Fertiliser | Add here -> | Electrification | Add here -> | MWth | Add here -> |  |  | Biomass (high quality) |  |  | Add here -> |  |  | NOx |  |  | Global
| Industry: Generic | Add here -> |  | Add here -> |  | Add here -> |  |  | Biomass (manure) |  |  |  |  | Add here ->
| Industry: Iron and steel | Add here -> |  | Add here -> |  | Add here -> |  |  | Biomass (starch) |  |  |  |  | Add here ->
| Industry: Non ETS | Add here -> |  | Add here -> |  |  |  |  | Biomass (sugars) |  |  |  |  | Add here ->
| Industry: Petrochemics | Add here -> |  | Add here -> |  |  |  |  | Biomass (waste biogenic) |  |  |  |  | Add here ->
| Mobile machinery | [7 empty] | Biomass (wet streams) |  |  |  |  | Add here ->
| Refineries | [7 empty] | Biomass (wood abroad)
| Trade, services and utilities | [7 empty] | Biomass (wood interior)
| Transport | [7 empty] | Biomass (wood)
Add here -> | CCS | [7 empty] | Bio-waste gases
Add here -> | [8 empty] | Blast furnace gas
Add here -> | [8 empty] | CCF gas
Add here -> | [8 empty] | Chemical residual gas
Add here -> | [8 empty] | Coal
Coke
Coke oven gas
Coking coal
Diesel
Electricity
Energy content manure
Fermentation gas
Gasoline
Geothermal heat
Heat
Heavy fuel oil
Hydrogen
Import electricity
Injection coal
LPG
Natural gas
Natural gas feedstock
Oil
Oil excluding gases
Oil raw materials
Other bio-oil products
Other oil products
Residual gases
Solar energy
Synthetic fuels
Uranium
Waste (non-biogenic)
Wind energy
[8 empty] | Add here -> | Benzine
[8 empty] | Add here -> | Bio-ethanol
[8 empty] | Add here -> | Coal excluding gases
[8 empty] | Add here -> | Electricity import
[8 empty] | Add here -> | Fuel oil
[8 empty] | Add here -> | High Pressure Steam
[8 empty] | Add here -> | Hydro
[8 empty] | Add here -> | Kerosene
[8 empty] | Add here -> | Oil feedstock
[8 empty] | Add here -> | Oil products
[8 empty] | Add here -> | Other gases
[8 empty] | Add here -> | Propane
[8 empty] | Add here -> | SNG
[8 empty] | Add here -> | Steam

## Calculations (hidden)
Cost breakdown
Date | 2 October 2018
Source | Wieringa, E. (2015) Financial feasibility of using an electric steam boiler in a mutlifuel steam production set and providing grid flexibility
Description | Breakdown of CAPEX according to internship thesis of Wieringa
Electric boiler size (MW) | 15.77
| Unit | Bio boiler | Electric boiler | Gas boiler
Life cycle (years) | Yrs | 12 | 20 | 20
Development cost | EUR_2015 | 250000 | 50000 | 50000
Capital expenses | EUR_2015 | 10000000 | 800000 | 500000
Grid connection | EUR_2015 |  | 300000
Operational expenses | EUR_2015 |  | 250000
| Electric boiler (EUR/MW) | Electric boiler (MEUR/MW)
Development cost | 3170.577 | 0.0031706
Capital expenses | 50729.2327 | 0.050729
Grid connection | 19023.4623 | 0.019023
Total | 72923.272
Potential
Date | 22 October 2018
Source | ECN (2017) Dutch program for the acceleration of sustainable heat management in industry
Description | Potential application of electric/electrode boilers in Dutch industry
Parameter | Unit | Value
Heat consumption Dutch industry <200 deg C that can be covered by heat pumps | PJ | 150
Electric boiler maximum load hours | hours/yr | 8760
Maximum potential electric boiler capacity for Dutch industry | MWth | 4756.4688
Parameter | Unit | Value
Average_efficiency el. Boiler | GJth/Gjel | 0.99
Efficiency el. Boiler low | GJth/Gjel | 0.9
Note on E17: R.P. de Smidt: Do we have information where Wieringa got the capital expenses from? 50,7 euro/kW sounds like an electrode boiler to me...